## Tank Farm
Data # | Processor OEM Tag | TransferTag | Data Concentrator Tag | Value | Path IP | Message | Python Variable Name
Faults
1 | SONITROL_ALM1 |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].0 | 1 | 10.168.100.101 | Boilers Faulted
2 | SONITROL_ALM2 |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].1 | 1 | 10.168.100.101 | HWS 1,2,or 3 High Temp
3 | SONITROL_ALM3 |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].2 | 1 | 10.168.100.101 | HWS 1,2,or 3 Low Temp
4 | BOILER1_STACK |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].3 | 1 | 10.168.100.101 | Boiler 1 Fault
5 | BOILER2_STACK |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].4 | 1 | 10.168.100.101 | Boiler 2 Fault
6 | TCV010.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].5 | 1 | 10.168.100.101 | HWS 1 Temp Control Valve Fault
7 | TCV020.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].6 | 1 | 10.168.100.101 | HWS 2 Temp Control Valve Fault
8 | TCV030.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].7 | 1 | 10.168.100.101 | HWS 3 Temp Control Valve Fault
9 | COND_PUMP1_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].8 | 1 | 10.168.100.101 | Condensate Return Pump P030 Insufficient Flow
10 | COND_PUMP1_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].9 | 1 | 10.168.100.101 | Condensate Return Pump P031 Insufficient Flow
11 | COND_PUMP_040_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].10 | 1 | 10.168.100.101 | Condensate Return Pump P040 Insufficient Flow
12 | COND_PUMP_041_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].11 | 1 | 10.168.100.101 | Condensate Return Pump P041 Insufficient Flow
13 | P010.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].12 | 1 | 10.168.100.101 | HWS1 P010 Pump Fault
14 | P020.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].13 | 1 | 10.168.100.101 | HWS2 P020 Pump Fault
15 | P030.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].14 | 1 | 10.168.100.101 | Condensate Return Pump P030 Fault
16 | P031.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].15 | 1 | 10.168.100.101 | Condensate Return Pump P031 Fault
17 | P040.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].16 | 1 | 10.168.100.101 | Condensate Return Pump P040 Fault
18 | P041.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].17 | 1 | 10.168.100.101 | Condensate Return Pump P041 Fault
19 | P001.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[0].18 | 1 | 10.168.100.101 | HWS3 P001 Pump Fault
20 | P010.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].0 | 1 | 10.168.100.101 | P010 Disconnect Open
21 | P010.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].1 | 1 | 10.168.100.101 | P010 Failed To Run
22 | P010.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].2 | 1 | 10.168.100.101 | P010 Failed to Stop
23 | P010.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].3 | 1 | 10.168.100.101 | P010 Overload
24 | P011.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].4 | 1 | 10.168.100.101 | P011 Disconnect Open
25 | P011.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].5 | 1 | 10.168.100.101 | P011 Failed To Run
26 | P011.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].6 | 1 | 10.168.100.101 | P011 Failed to Stop
27 | P011.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].7 | 1 | 10.168.100.101 | P011 Overload
28 | P012.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].8 | 1 | 10.168.100.101 | P012 Disconnect Open
29 | P012.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].9 | 1 | 10.168.100.101 | P012 Failed To Run
30 | P012.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].10 | 1 | 10.168.100.101 | P012 Failed to Stop
31 | P012.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].11 | 1 | 10.168.100.101 | P012 Overload
32 | P013.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].12 | 1 | 10.168.100.101 | P013 Disconnect Open
33 | P013.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].13 | 1 | 10.168.100.101 | P013 Failed To Run
34 | P013.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].14 | 1 | 10.168.100.101 | P013 Failed to Stop
35 | P013.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].15 | 1 | 10.168.100.101 | P013 Overload
36 | P014.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].16 | 1 | 10.168.100.101 | P014 Disconnect Open
37 | P014.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].17 | 1 | 10.168.100.101 | P014 Failed To Run
38 | P014.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].18 | 1 | 10.168.100.101 | P014 Failed to Stop
39 | P014.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].19 | 1 | 10.168.100.101 | P014 Overload
40 | P020.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].20 | 1 | 10.168.100.101 | P020 Disconnect Open
41 | P020.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].21 | 1 | 10.168.100.101 | P020 Failed To Run
42 | P020.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].22 | 1 | 10.168.100.101 | P020 Failed to Stop
43 | P020.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].23 | 1 | 10.168.100.101 | P020 Overload
44 | P021.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].24 | 1 | 10.168.100.101 | P021 Disconnect Open
45 | P021.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].25 | 1 | 10.168.100.101 | P021 Failed To Run
46 | P021.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].26 | 1 | 10.168.100.101 | P021 Failed to Stop
47 | P021.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].27 | 1 | 10.168.100.101 | P021 Overload
48 | P022.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].28 | 1 | 10.168.100.101 | P022 Disconnect Open
49 | P022.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].29 | 1 | 10.168.100.101 | P022 Failed To Run
50 | P022.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].30 | 1 | 10.168.100.101 | P022 Failed to Stop
51 | P022.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[1].31 | 1 | 10.168.100.101 | P022 Overload
52 | P024.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].0 | 1 | 10.168.100.101 | P024 Disconnect Open
53 | P024.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].1 | 1 | 10.168.100.101 | P024 Failed To Run
54 | P024.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].2 | 1 | 10.168.100.101 | P024 Failed to Stop
55 | P024.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].3 | 1 | 10.168.100.101 | P024 Overload
56 | P025.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].4 | 1 | 10.168.100.101 | P025 Disconnect Open
57 | P025.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].5 | 1 | 10.168.100.101 | P025 Failed To Run
58 | P025.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].6 | 1 | 10.168.100.101 | P025 Failed to Stop
59 | P025.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].7 | 1 | 10.168.100.101 | P025 Overload
60 | P100.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].8 | 1 | 10.168.100.101 | P100 Disconnect Open
61 | P100.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].9 | 1 | 10.168.100.101 | P100 Failed To Run
62 | P100.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].10 | 1 | 10.168.100.101 | P100 Failed to Stop
63 | P100.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].11 | 1 | 10.168.100.101 | P100 Overload
64 | P200.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].12 | 1 | 10.168.100.101 | P200 Disconnect Open
65 | P200.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].13 | 1 | 10.168.100.101 | P200 Failed To Run
66 | P200.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].14 | 1 | 10.168.100.101 | P200 Failed to Stop
67 | P200.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].15 | 1 | 10.168.100.101 | P200 Overload
68 | P300.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].16 | 1 | 10.168.100.101 | P300 Disconnect Open
69 | P300.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].17 | 1 | 10.168.100.101 | P300 Failed To Run
70 | P300.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].18 | 1 | 10.168.100.101 | P300 Failed to Stop
71 | P300.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].19 | 1 | 10.168.100.101 | P300 Overload
72 | P500.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].20 | 1 | 10.168.100.101 | P500 Disconnect Open
73 | P500.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].21 | 1 | 10.168.100.101 | P500 Failed To Run
74 | P500.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].22 | 1 | 10.168.100.101 | P500 Failed to Stop
75 | P500.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].23 | 1 | 10.168.100.101 | P500 Overload
76 | AG105.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].24 | 1 | 10.168.100.101 | AG105 Disconnect Open
77 | AG105.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].25 | 1 | 10.168.100.101 | AG105 Failed To Run
78 | AG105.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].26 | 1 | 10.168.100.101 | AG105 Failed To Stop
79 | AG105.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].27 | 1 | 10.168.100.101 | AG105 Overload
80 | AG205.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].28 | 1 | 10.168.100.101 | AG205 Disconnect Open
81 | AG205.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].29 | 1 | 10.168.100.101 | AG205 Failed To Run
82 | AG205.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].30 | 1 | 10.168.100.101 | AG205 Failed To Stop
83 | AG205.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[2].31 | 1 | 10.168.100.101 | AG205 Overload
84 | AG305.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].0 | 1 | 10.168.100.101 | AG305 Disconnect Open
85 | AG305.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].1 | 1 | 10.168.100.101 | AG305 Failed To Run
86 | AG305.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].2 | 1 | 10.168.100.101 | AG305 Failed To Stop
87 | AG305.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].3 | 1 | 10.168.100.101 | AG305 Overload
88 | AG405.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].4 | 1 | 10.168.100.101 | AG405 Disconnect Open
89 | AG405.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].5 | 1 | 10.168.100.101 | AG405 Failed To Run
90 | AG405.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].6 | 1 | 10.168.100.101 | AG405 Failed To Stop
91 | AG405.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].7 | 1 | 10.168.100.101 | AG405 Overload
92 | AV130.CTRL.FLT_FCL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].8 | 1 | 10.168.100.101 | AV130 Failed To Close
93 | AV130.CTRL.FLT_FOP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].9 | 1 | 10.168.100.101 | AV130 Failed To Open
94 | AV220.CTRL.FLT_FCL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].10 | 1 | 10.168.100.101 | AV220 Failed To Close
95 | AV220.CTRL.FLT_FOP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].11 | 1 | 10.168.100.101 | AV220 Failed To Open
96 | AV300.CTRL.FLT_FCL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].12 | 1 | 10.168.100.101 | AV300 Failed To Close
97 | AV300.CTRL.FLT_FOP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].13 | 1 | 10.168.100.101 | AV300 Failed To Open
98 | AV306.CTRL.FLT_FCL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].14 | 1 | 10.168.100.101 | AV306 Failed To Close
99 | AV306.CTRL.FLT_FOP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].15 | 1 | 10.168.100.101 | AV306 Failed To Open
100 | AV400.CTRL.FLT_FCL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].16 | 1 | 10.168.100.101 | AV400 Failed To Close
101 | AV400.CTRL.FLT_FOP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].17 | 1 | 10.168.100.101 | AV400 Failed To Open
102 | AV406.CTRL.FLT_FCL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].18 | 1 | 10.168.100.101 | AV406 Failed To Close
103 | AV406.CTRL.FLT_FOP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].19 | 1 | 10.168.100.101 | AV406 Failed To Open
104 | PT100.STS.HI |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].20 | 1 | 10.168.100.101 | Tank 1 Unload Line PSI High
105 | PT200.STS.HI |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].21 | 1 | 10.168.100.101 | Tank 2 Unload Line PSI High
106 | PT300.STS.HI |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].22 | 1 | 10.168.100.101 | Tank 3 Unload Line PSI High
107 | PT400.STS.HI |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].23 | 1 | 10.168.100.101 | Tank 4 Unload Line PSI High
108 | PT500.STS.HI |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].24 | 1 | 10.168.100.101 | Tank 5 Unload Line PSI High
109 | HWS1_HI_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].25 | 1 | 10.168.100.101 | HWS1 High Temp
110 | HWS1_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].26 | 1 | 10.168.100.101 | HWS1 Low Temp
111 | HWS2_HI_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].27 | 1 | 10.168.100.101 | HWS2 High Temp
112 | HWS2_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].28 | 1 | 10.168.100.101 | HWS2 Low Temp
113 | SONITROL_ALM1 |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].29 | 1 | 10.168.100.101 | Sonitrol Alarm 1
114 | Spare |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].30 | 1 | 10.168.100.101 | Spare
115 | Spare |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[3].31 | 1 | 10.168.100.101 | Spare
116 | Spare |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].0 | 1 | 10.168.100.101 | Spare
117 | Spare |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].1 | 1 | 10.168.100.101 | Spare
118 | Spare |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].2 | 1 | 10.168.100.101 | Spare
119 | LOOP1_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].3 | 1 | 10.168.100.101 | Loop 1 Low Temp
120 | LOOP2_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].4 | 1 | 10.168.100.101 | Loop 2 Low Temp
121 | LOOP3_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].5 | 1 | 10.168.100.101 | Loop 3 Low Temp
122 | LOOP8_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].6 | 1 | 10.168.100.101 | Loop 8 Low Temp
123 | LOOP9_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].7 | 1 | 10.168.100.101 | Loop 9 Low Temp
124 | COND_PUMP_040_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].8 | 1 | 10.168.100.101 | Cond Pump 3 Insufficient Flow
125 | COND_PUMP_041_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].9 | 1 | 10.168.100.101 | Cond Pump 4 Insufficient Flow
126 | COND_PUMP1_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].10 | 1 | 10.168.100.101 | Cond Pump 1 Insufficient Flow
127 | COND_PUMP2_INS_FLOW |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].11 | 1 | 10.168.100.101 | Cond Pump 2 Insufficient Flow
128 | P001.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].12 | 1 | 10.168.100.101 | P001 Disconnect Open
129 | P001.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].13 | 1 | 10.168.100.101 | P001 Failed To Run
130 | P001.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].14 | 1 | 10.168.100.101 | P001 Failed To Stop
131 | P001.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].15 | 1 | 10.168.100.101 | P001 Overload
132 | P018.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].16 | 1 | 10.168.100.101 | P018 Disconnect Open
133 | P018.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].17 | 1 | 10.168.100.101 | P018 Failed To Run
134 | P018.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].18 | 1 | 10.168.100.101 | P018 Failed To Stop
135 | P018.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].19 | 1 | 10.168.100.101 | P018 Overload
136 | P019.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].20 | 1 | 10.168.100.101 | P019 Disconnect Open
137 | P019.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].21 | 1 | 10.168.100.101 | P019 Failed To Run
138 | P019.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].22 | 1 | 10.168.100.101 | P019 Failed To Stop
139 | P019.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].23 | 1 | 10.168.100.101 | P019 Overload
140 | P028.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].24 | 1 | 10.168.100.101 | P028 Disconnect Open
141 | P028.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].25 | 1 | 10.168.100.101 | P028 Failed To Run
142 | P028.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].26 | 1 | 10.168.100.101 | P028 Failed To Stop
143 | P028.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].27 | 1 | 10.168.100.101 | P028 Overload
144 | P029.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].28 | 1 | 10.168.100.101 | P029 Disconnect Open
145 | P029.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].29 | 1 | 10.168.100.101 | P029 Failed To Run
146 | P029.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].30 | 1 | 10.168.100.101 | P029 Failed To Stop
147 | P029.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[4].31 | 1 | 10.168.100.101 | P029 Overload
148 | Spare |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].0 | 1 | 10.168.100.101 | Spare
149 | Spare |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].1 | 1 | 10.168.100.101 | Spare
150 | P800.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].2 | 1 | 10.168.100.101 | P800 Disconnect Open
151 | P800.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].3 | 1 | 10.168.100.101 | P800 Failed To Run
152 | P800.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].4 | 1 | 10.168.100.101 | P800 Failed To Stop
153 | P800.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].5 | 1 | 10.168.100.101 | P800 Overload
154 | P900.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].6 | 1 | 10.168.100.101 | P900 Disconnect Open
155 | P900.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].7 | 1 | 10.168.100.101 | P900 Failed To Run
156 | P900.CTRL.FLT_FST |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].8 | 1 | 10.168.100.101 | P900 Failed To Stop
157 | P900.CTRL.FLT_MOL |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].9 | 1 | 10.168.100.101 | P900 Overload
158 | AG805.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].10 | 1 | 10.168.100.101 | AG805 Disconnect Open
159 | AG805.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].11 | 1 | 10.168.100.101 | AG805 Failed To Run
160 | AG905.CTRL.FLT_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].12 | 1 | 10.168.100.101 | AG905 Disconnect Open
161 | AG905.CTRL.FLT_FRF |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].13 | 1 | 10.168.100.101 | AG905 Failed To Run
162 | HWS3_HI_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].14 | 1 | 10.168.100.101 | HWS3 High Temp
163 | HWS3_LOW_TEMP |  | [Skynet]ComData_TankFarm_To_Skynet.Fault_Data[5].15 | 1 | 10.168.100.101 | HWS3 Low Temp
Data# |  |  | Tag name | Value | Path IP | Description | Python Variable Name
Status Bits
164 | SYSTEM ENABLED |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].0 | 1 | 10.168.100.101 | System Enabled | tank_farm_system_enabled
165 | HWS1.STS.RUNNING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].1 | 1 | 10.168.100.101 | HWS1 Running | tank_farm_hws1_running
166 | HWS2.STS.RUNNING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].2 | 1 | 10.168.100.101 | HWS2 Running | tank_farm_hws1_running
167 | HWS3.STS.RUNNING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].3 | 1 | 10.168.100.101 | HWS3 Running | tank_farm_hws1_running
168 | BOILER1_STATUS |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].4 | 1 | 10.168.100.101 | Boiler 1 Running | tank_farm_boiler_1_running
169 | BOILER2_STATUS |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].5 | 1 | 10.168.100.101 | Boiler 2 Running | tank_farm_boiler_2_running
170 | P010.CTRL.IN_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].6 | 1 | 10.168.100.101 | HWS1 Pump P010 Running | tank_farm_hws1_pump_p010_running
171 | P020.CTRL.IN_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].7 | 1 | 10.168.100.101 | HWS2 Pump P020 Running | tank_farm_hws2_pump_p020_running
172 | P030.CTRL.IN_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].8 | 1 | 10.168.100.101 | Condensate Pump P030 Running | tank_farm_condensate_pump_p030_running
173 | P031.CTRL.IN_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].9 | 1 | 10.168.100.101 | Condensate Pump P031 Running | tank_farm_condensate_pump_p031_running
174 | COND_TK_HLV |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].10 | 1 | 10.168.100.101 | Condensate Tank 1 High Level | tank_farm_condensate_tank_1_high_level
175 | HWS3:3:I.1 |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].11 | 1 | 10.168.100.101 | Condensate Tank 2 High Level | tank_farm_condensate_tank_2_high_level
176 | P001.CTRL.IN_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].12 | 1 | 10.168.100.101 | HWS3 Pump P001 Running | tank_farm_hws3_pump_p001_running
177 | P040.CTRL.IN_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].13 | 1 | 10.168.100.101 | Condensate Pump P040 Running | tank_farm_condensate_pump_p040_running
178 | P041.CTRL.IN_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].14 | 1 | 10.168.100.101 | Condensate Pump P041 Running | tank_farm_condensate_pump_p041_running
179 | P100.CTRL.STS_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].15 | 1 | 10.168.100.101 | Chocolate Loop 1 Pump Running | tank_farm_chocolate_loop_1_pump_running
180 | P200.CTRL.STS_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].16 | 1 | 10.168.100.101 | Chocolate Loop 2 Pump Running | tank_farm_chocolate_loop_2_pump_running
181 | P300.CTRL.STS_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].17 | 1 | 10.168.100.101 | Chocolate Loop 3 Pump Running | tank_farm_chocolate_loop_3_pump_running
182 | P500.CTRL.STS_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].18 | 1 | 10.168.100.101 | Glucose Pump Running | tank_farm_glucose_pump_running
183 | P011.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].19 | 1 | 10.168.100.101 | P011 Running | tank_farm_p011_running
184 | P012.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].20 | 1 | 10.168.100.101 | P012 Running | tank_farm_p012_running
185 | P013.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].21 | 1 | 10.168.100.101 | P013 Running | tank_farm_p013_running
186 | P014.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].22 | 1 | 10.168.100.101 | P014 Running | tank_farm_p014_running
187 | P021.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].23 | 1 | 10.168.100.101 | P021 Running | tank_farm_p021_running
188 | P022.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].24 | 1 | 10.168.100.101 | P022 Running | tank_farm_p022_running
189 | P024.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].25 | 1 | 10.168.100.101 | P024 Running | tank_farm_p024_running
190 | P025.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].26 | 1 | 10.168.100.101 | P025 Running | tank_farm_p025_running
191 | P028.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].27 | 1 | 10.168.100.101 | P028 Running | tank_farm_p028_running
192 | P029.CTRL.OUT_RUN |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].28 | 1 | 10.168.100.101 | P029 Running | tank_farm_p029_running
193 | P100.CTRL.IN_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].29 | 1 | 10.168.100.101 | P100 Disconnect Closed | tank_farm_p100_disconnect_closed
194 | P200.CTRL.IN_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].30 | 1 | 10.168.100.101 | P200 Disconnect Closed | tank_farm_p200_disconnect_closed
195 | P300.CTRL.IN_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[0].31 | 1 | 10.168.100.101 | P300 Disconnect Closed | tank_farm_p300_disconnect_closed
196 | P500.CTRL.IN_DSC |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].0 | 1 | 10.168.100.101 | P500 Disconnect Closed
197 | P100.CTRL.EnableIn |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].1 | 1 | 10.168.100.101 | P100 Enabled
198 | P200.CTRL.EnableIn |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].2 | 1 | 10.168.100.101 | P200 Enabled
199 | P300.CTRL.EnableIn |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].3 | 1 | 10.168.100.101 | P300 Enabled
200 | P500.CTRL.EnableIn |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].4 | 1 | 10.168.100.101 | P500 Enabled
201 | P011.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].5 | 1 | 10.168.100.101 | P011 Faulted
202 | P012.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].6 | 1 | 10.168.100.101 | P012 Faulted
203 | P013.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].7 | 1 | 10.168.100.101 | P013 Faulted
204 | P014.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].8 | 1 | 10.168.100.101 | P014 Faulted
205 | P021.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].9 | 1 | 10.168.100.101 | P021 Faulted
206 | P022.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].10 | 1 | 10.168.100.101 | P022 Faulted
207 | P024.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].11 | 1 | 10.168.100.101 | P024 Faulted
208 | P025.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].12 | 1 | 10.168.100.101 | P025 Faulted
209 | P028.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].13 | 1 | 10.168.100.101 | P028 Faulted
210 | P029.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].14 | 1 | 10.168.100.101 | P029 Faulted
211 | P100.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].15 | 1 | 10.168.100.101 | P100 Faulted
212 | P200.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].16 | 1 | 10.168.100.101 | P200 Faulted
213 | P300.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].17 | 1 | 10.168.100.101 | P300 Faulted
214 | P500.CTRL.STS_FLT |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[1].18 | 1 | 10.168.100.101 | P500 Faulted
215 | HWS1.STS.IDLE |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 0 | 10.168.100.101 | HWS1 Idle
216 | HWS1.STS.STARTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 1 | 10.168.100.101 | HWS1 Starting
217 | HWS1.STS.RUNNING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 2 | 10.168.100.101 | HWS1 Running
218 | HWS1.STS.STOPPED |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 3 | 10.168.100.101 | HWS1 Stopped
219 | HWS1.STS.STOPPING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 4 | 10.168.100.101 | HWS1 Stopping
220 | HWS1.STS.RESETTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 5 | 10.168.100.101 | HWS1 Resetting
221 | HWS1.STS.ABORTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 6 | 10.168.100.101 | HWS1 Aborting
222 | HWS1.STS.FAULTED |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 7 | 10.168.100.101 | HWS1 Faulted
223 | HWS1.STS.HELD |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[30].0 | 8 | 10.168.100.101 | HWS1 Held
224 | HWS2.STS.IDLE |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 0 | 10.168.100.101 | HWS2 Idle
225 | HWS2.STS.STARTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 1 | 10.168.100.101 | HWS2 Starting
226 | HWS2.STS.RUNNING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 2 | 10.168.100.101 | HWS2 Running
227 | HWS2.STS.STOPPED |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 3 | 10.168.100.101 | HWS2 Stopped
228 | HWS2.STS.STOPPING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 4 | 10.168.100.101 | HWS2 Stopping
229 | HWS2.STS.RESETTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 5 | 10.168.100.101 | HWS2 Resetting
230 | HWS2.STS.ABORTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 6 | 10.168.100.101 | HWS2 Aborting
231 | HWS2.STS.FAULTED |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 7 | 10.168.100.101 | HWS2 Faulted
232 | HWS2.STS.HELD |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[31].0 | 8 | 10.168.100.101 | HWS2 Held
233 | HWS3.STS.IDLE |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 0 | 10.168.100.101 | HWS3 Idle
234 | HWS3.STS.STARTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 1 | 10.168.100.101 | HWS3 Starting
235 | HWS3.STS.RUNNING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 2 | 10.168.100.101 | HWS3 Running
236 | HWS3.STS.STOPPED |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 3 | 10.168.100.101 | HWS3 Stopped
237 | HWS3.STS.STOPPING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 4 | 10.168.100.101 | HWS3 Stopping
238 | HWS3.STS.RESETTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 5 | 10.168.100.101 | HWS3 Resetting
239 | HWS3.STS.ABORTING |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 6 | 10.168.100.101 | HWS3 Aborting
240 | HWS3.STS.FAULTED |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 7 | 10.168.100.101 | HWS3 Faulted
241 | HWS3.STS.HELD |  | [Skynet]ComData_TankFarm_To_Skynet.Status_Bits[32].0 | 8 | 10.168.100.101 | HWS3 Held
Setpoints
| HWS1.SP.MISC_SP[0] |  | [Skynet]ComData_TankFarm_To_Skynet.Setpoint_Values[0] | Var | 10.168.100.101 | HWS1 Setpoint | tank_farm_hws1_setpoint
| HWS2.SP.MISC_SP[0] |  | [Skynet]ComData_TankFarm_To_Skynet.Setpoint_Values[1] | Var | 10.168.100.101 | HWS2 Setpoint | tank_farm_hws2_setpoint
| HWS3.SP.MISC_SP[0] |  | [Skynet]ComData_TankFarm_To_Skynet.Setpoint_Values[2] | Var | 10.168.100.101 | HWS3 Setpoint | tank_farm_hws3_setpoint
Process Values
| TCV010.CTRL.OUT_POS | . | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[0] | Var | 10.168.100.101 | HWS1 Output Valve Position | tank_farm_hws1_output_valve_position
| TCV020.CTRL.OUT_POS |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[1] | Var | 10.168.100.101 | HWS2 Output Valve Position | tank_farm_hws2_output_valve_position
| TCV030.CTRL.OUT_POS |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[2] | Var | 10.168.100.101 | HWS3 Output Valve Position | tank_farm_hws3_output_valve_position
| TT010.VAL.ACT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[3] | Var | 10.168.100.101 | HWS1 Output Temperature | tank_farm_hws1_output_temp
| TT011.VAL.ACT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[4] | Var | 10.168.100.101 | HWS1 Return Temperature | tank_farm_hws1_return_temp
| TT020.VAL.ACT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[5] | Var | 10.168.100.101 | HWS2 Output Temperature | tank_farm_hws2_output_temp
| TT021.VAL.ACT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[6] | Var | 10.168.100.101 | HWS2 Return Temperature | tank_farm_hws2_return_temp
| TT030.VAL.ACT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[7] | Var | 10.168.100.101 | HWS3 Output Temperature | tank_farm_hws3_output_temp
| TT031.VAL.ACT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[8] | Var | 10.168.100.101 | HWS3 Return Temperature | tank_farm_hws3_return_temp
| LIC101.CTRL.OUT.PERCENT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[9] | Var | 10.168.100.101 | Tank 1 Level (%) | tank_farm_tank_1_level_percentage
| LIC201.CTRL.OUT.PERCENT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[10] | Var | 10.168.100.101 | Tank 2 Level (%) | tank_farm_tank_2_level_percentage
| LIC301.CTRL.OUT.PERCENT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[11] | Var | 10.168.100.101 | Tank 3 Level (%) | tank_farm_tank_3_level_percentage
| LIC401.CTRL.OUT.PERCENT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[12] | Var | 10.168.100.101 | Tank 4 Level (%) | tank_farm_tank_4_level_percentage
| LIC501.CTRL.OUT.PERCENT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[13] | Var | 10.168.100.101 | Tank 5 Level (%) | tank_farm_tank_5_level_percentage
| LIC101.CTRL.OUT.WT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[14] | Var | 10.168.100.101 | Tank 1 LBS
| LIC201.CTRL.OUT.WT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[15] | Var | 10.168.100.101 | Tank 2 LBS
| LIC301.CTRL.OUT.WT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[16] | Var | 10.168.100.101 | Tank 3 LBS
| LIC401.CTRL.OUT.WT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[17] | Var | 10.168.100.101 | Tank 4 LBS
| LIC501.CTRL.OUT.WT |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[18] | Var | 10.168.100.101 | Tank 5 LBS
| LIC101.CTRL.OUT.VOL |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[19] | Var | 10.168.100.101 | Tank 1 (kg) | tank_farm_tank_1__kg
| LIC201.CTRL.OUT.VOL |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[20] | Var | 10.168.100.101 | Tank 2 (kg) | tank_farm_tank_2_kg
| LIC301.CTRL.OUT.VOL |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[21] | Var | 10.168.100.101 | Tank 3 (kg) | tank_farm_tank_3_kg
| LIC401.CTRL.OUT.VOL |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[22] | Var | 10.168.100.101 | Tank 4 (kg) | tank_farm_tank_4__kg
| LIC501.CTRL.OUT.VOL |  | [Skynet]ComData_TankFarm_To_Skynet.Process_Values[23] | Var | 10.168.100.101 | Tank 5 (kg) | tank_farm_tank_5__kg

## Clayton SG1 (hidden)
Alarm # | Processor OEM Tag | TransferTag | Data Concentrator Tag | Value | Path IP | Message
1 | [PLC]B3:4.0 | N15:10.0 | [Skynet]ComData_Clayton_SG1_INT[10].0 | 1 | 10.168.100.110 | Steam Pressure High Limit
2 | [PLC]B3:4.1 | N15:10.1 | [Skynet]ComData_Clayton_SG1_INT[10].1 | 1 | 10.168.100.110 | Steam Coil Temp High Limit
3 | [PLC]B3:4.2 | N15:10.2 | [Skynet]ComData_Clayton_SG1_INT[10].2 | 1 | 10.168.100.110 | Separator Temp High Limit
4 | [PLC]B3:4.3 | N15:10.3 | [Skynet]ComData_Clayton_SG1_INT[10].3 | 1 | 10.168.100.110 | Burner Volute Temp High Limit
5 | [PLC]B3:4.4 | N15:10.4 | [Skynet]ComData_Clayton_SG1_INT[10].4 | 1 | 10.168.100.110 | Gas Pressure High/Low
6 | [PLC]B3:4.5 | N15:10.5 | [Skynet]ComData_Clayton_SG1_INT[10].5 | 1 | 10.168.100.110 | VSD Faulted
7 | [PLC]B3:4.6 | N15:10.6 | [Skynet]ComData_Clayton_SG1_INT[10].6 | 1 | 10.168.100.110 | Motor Overload
8 | [PLC]B3:4.7 | N15:10.7 | [Skynet]ComData_Clayton_SG1_INT[10].7 | 1 | 10.168.100.110 | Oil Level High or Low
9 | [PLC]B3:4.8 | N15:10.8 | [Skynet]ComData_Clayton_SG1_INT[10].8 | 1 | 10.168.100.110 | Pilot Fuel Low Limit
10 | [PLC]B3:4.9 | N15:10.9 | [Skynet]ComData_Clayton_SG1_INT[10].9 | 1 | 10.168.100.110 | Burner Fuel Low Limit
11 | [PLC]B3:4.10 | N15:10.10 | [Skynet]ComData_Clayton_SG1_INT[10].10 | 1 | 10.168.100.110 | Atomizing air Low Limit
12 | [PLC]B3:4.11 | N15:10.11 | [Skynet]ComData_Clayton_SG1_INT[10].11 | 1 | 10.168.100.110 | Separator water Level High Limit
13 | [PLC]B3:4.12 | N15:10.12 | [Skynet]ComData_Clayton_SG1_INT[10].12 | 1 | 10.168.100.110 | Intake Air Pressure Switch
14 | [PLC]B3:4.13 | N15:10.13 | [Skynet]ComData_Clayton_SG1_INT[10].13 | 1 | 10.168.100.110 | Booster Pump Failure
15 | [PLC]B3:4.14 | N15:10.14 | [Skynet]ComData_Clayton_SG1_INT[10].14 | 1 | 10.168.100.110 | Damper Failure
16 | [PLC]B3:4.15 | N15:10.15 | [Skynet]ComData_Clayton_SG1_INT[10].15 | 1 | 10.168.100.110 | Burner Safeguard Tripped
Data# |  |  | Tag name | Value | Path IP | Decription
Inputs
1 | [PLC]I:0.0 | N15:0.0 | [Skynet]ComData_Clayton_SG1_INT[0].0 | 1 | 10.168.100.110 | E-Stop Circuit
2 | [PLC]I:0.1 | N15:0.1 | [Skynet]ComData_Clayton_SG1_INT[0].1 | 1 | 10.168.100.110 | Start
3 | [PLC]I:0.2 | N15:0.2 | [Skynet]ComData_Clayton_SG1_INT[0].2 | 1 | 10.168.100.110 | Limit Pressure Switch
4 | [PLC]I:0.3 | N15:0.3 | [Skynet]ComData_Clayton_SG1_INT[0].3 | 1 | 10.168.100.110 | Main Temperature Limit Controller
5 | [PLC]I:0.4 | N15:0.4 | [Skynet]ComData_Clayton_SG1_INT[0].4 | 1 | 10.168.100.110 | Auxilliary Thermostat switch
6 | [PLC]I:0.5 | N15:0.5 | [Skynet]ComData_Clayton_SG1_INT[0].5 | 1 | 10.168.100.110 | Electronic Safety Control Alarm
7 | [PLC]I:0.6 | N15:0.6 | [Skynet]ComData_Clayton_SG1_INT[0].6 | 1 | 10.168.100.110 | Blower
8 | [PLC]I:0.7 | N15:0.7 | [Skynet]ComData_Clayton_SG1_INT[0].7 | 1 | 10.168.100.110 | VSD Fault
9 | [PLC]I:0.8 | N15:0.8 | [Skynet]ComData_Clayton_SG1_INT[0].8 | 1 | 10.168.100.110 | Motor Overload
10 | [PLC]I:0.9 | N15:0.9 | [Skynet]ComData_Clayton_SG1_INT[0].9 | 1 | 10.168.100.110 | Ignition
11 | [PLC]I:0.10 | N15:0.10 | [Skynet]ComData_Clayton_SG1_INT[0].10 | 1 | 10.168.100.110 | Stack Damper Limit Switch
12 | [PLC]I:0.11 | N15:0.11 | [Skynet]ComData_Clayton_SG1_INT[0].11 | 1 | 10.168.100.110 | Fuel Valves
13 | [PLC]I:0.12 | N15:0.12 | [Skynet]ComData_Clayton_SG1_INT[0].12 | 1 | 10.168.100.110 | Pump Oil Level Switch
14 | [PLC]I:0.13 | N15:0.13 | [Skynet]ComData_Clayton_SG1_INT[0].13 | 1 | 10.168.100.110 | Spare
15 | [PLC]I:0.14 | N15:0.14 | [Skynet]ComData_Clayton_SG1_INT[0].14 | 1 | 10.168.100.110 | Spare
16 | [PLC]I:0.15 | N15:0.15 | [Skynet]ComData_Clayton_SG1_INT[0].15 | 1 | 10.168.100.110 | Spare
Outputs
18 | [PLC]O:0.0 | N15:8.0 | [Skynet]ComData_Clayton_SG1_INT[8].0 | 1 | 10.168.100.110 | Holding Relay
19 | [PLC]O:0.1 | N15:8.1 | [Skynet]ComData_Clayton_SG1_INT[8].1 | 1 | 10.168.100.110 | SPS
20 | [PLC]O:0.2 | N15:8.2 | [Skynet]ComData_Clayton_SG1_INT[8].2 | 1 | 10.168.100.110 | Spare
21 | [PLC]O:0.3 | N15:8.3 | [Skynet]ComData_Clayton_SG1_INT[8].3 | 1 | 10.168.100.110 | Audible Alarm
22 | [PLC]O:0.4 | N15:8.4 | [Skynet]ComData_Clayton_SG1_INT[8].4 | 1 | 10.168.100.110 | VSR Run Relay
23 | [PLC]O:0.5 | N15:8.5 | [Skynet]ComData_Clayton_SG1_INT[8].5 | 1 | 10.168.100.110 | Spare
24 | [PLC]O:0.6 | N15:8.6 | [Skynet]ComData_Clayton_SG1_INT[8].6 | 1 | 10.168.100.110 | Spare
25 | [PLC]O:0.7 | N15:8.7 | [Skynet]ComData_Clayton_SG1_INT[8].7 | 1 | 10.168.100.110 | Stack Damper Relay
26 | [PLC]O:0.8 | N15:8.8 | [Skynet]ComData_Clayton_SG1_INT[8].8 | 1 | 10.168.100.110 | Automatic Dump Valve
27 | [PLC]O:0.9 | N15:8.9 | [Skynet]ComData_Clayton_SG1_INT[8].9 | 1 | 10.168.100.110 | Makeup Water Valve
28 | [PLC]O:0.10 | N15:8.10 | [Skynet]ComData_Clayton_SG1_INT[8].10 | 1 | 10.168.100.110 | Spare
Mode
29 | [PLC]B3:0.1 | N15:9.0 | [Skynet]ComData_Clayton_SG1_INT[9].0 | 1 | 10.168.100.110 | Mode Fill / Run
30 | [PLC]B3:1.9 | N15:9.1 | [Skynet]ComData_Clayton_SG1_INT[9].1 | 1 | 10.168.100.110 | Mode Auto / Manual
31 | [PLC]B3:2.11 | N15:9.2 | [Skynet]ComData_Clayton_SG1_INT[9].2 | 1 | 10.168.100.110 | Mode Primary / Auxilliary
32 |  | N15:9.3 | [Skynet]ComData_Clayton_SG1_INT[9].3 | 1 | 10.168.100.110 | Spare
Analog
33 | [PLC]N7:1(*0064) | N16:1 | [Skynet]ComData_Clayton_SG1_REAL[1] | Var | 10.168.100.110 | Firing Rate
34 | [PLC]I:1.0 | N15:1 | [Skynet]ComData_Clayton_SG1_INT[1] | Var | 10.168.100.110 | System Steam Pressure
35 | [PLC]I:1.1 | N15:2 | [Skynet]ComData_Clayton_SG1_INT[2] | Var | 10.168.100.110 | Separator Steam Pressure
36 | [PLC]N7:22 | N15:3 | [Skynet]ComData_Clayton_SG1_INT[3] | Var | 10.168.100.110 | Op Hours MSR
37 | [PLC]N7:23 | N15:4 | [Skynet]ComData_Clayton_SG1_INT[4] | Var | 10.168.100.110 | OP Hours LSR
38 | [PLC]N10:8 | N15:5 | [Skynet]ComData_Clayton_SG1_INT[5] | var | 10.168.100.110 | VSD Output %

## Clayton SG2 (hidden)
Alarm # | Processor OEM Tag | TransferTag | Data Concentrator Tag | Value | Path IP | Message
1 | [PLC]B3:4.0 | N15:10.0 | [Skynet]ComData_Clayton SG2_INT[10].0 | 1 | 10.168.100.111 | Steam Pressure High Limit
2 | [PLC]B3:4.1 | N15:10.1 | [Skynet]ComData_Clayton SG2_INT[10].1 | 1 | 10.168.100.111 | Steam Coil Temp High Limit
3 | [PLC]B3:4.2 | N15:10.2 | [Skynet]ComData_Clayton SG2_INT[10].2 | 1 | 10.168.100.111 | Separator Temp High Limit
4 | [PLC]B3:4.3 | N15:10.3 | [Skynet]ComData_Clayton SG2_INT[10].3 | 1 | 10.168.100.111 | Burner Volute Temp High Limit
5 | [PLC]B3:4.4 | N15:10.4 | [Skynet]ComData_Clayton SG2_INT[10].4 | 1 | 10.168.100.111 | Gas Pressure High/Low
6 | [PLC]B3:4.5 | N15:10.5 | [Skynet]ComData_Clayton SG2_INT[10].5 | 1 | 10.168.100.111 | VSD Faulted
7 | [PLC]B3:4.6 | N15:10.6 | [Skynet]ComData_Clayton SG2_INT[10].6 | 1 | 10.168.100.111 | Motor Overload
8 | [PLC]B3:4.7 | N15:10.7 | [Skynet]ComData_Clayton SG2_INT[10].7 | 1 | 10.168.100.111 | Oil Level High or Low
9 | [PLC]B3:4.8 | N15:10.8 | [Skynet]ComData_Clayton SG2_INT[10].8 | 1 | 10.168.100.111 | Pilot Fuel Low Limit
10 | [PLC]B3:4.9 | N15:10.9 | [Skynet]ComData_Clayton SG2_INT[10].9 | 1 | 10.168.100.111 | Burner Fuel Low Limit
11 | [PLC]B3:4.10 | N15:10.10 | [Skynet]ComData_Clayton SG2_INT[10].10 | 1 | 10.168.100.111 | Atomizing air Low Limit
12 | [PLC]B3:4.11 | N15:10.11 | [Skynet]ComData_Clayton SG2_INT[10].11 | 1 | 10.168.100.111 | Separator water Level High Limit
13 | [PLC]B3:4.12 | N15:10.12 | [Skynet]ComData_Clayton SG2_INT[10].12 | 1 | 10.168.100.111 | Intake Air Pressure Switch
14 | [PLC]B3:4.13 | N15:10.13 | [Skynet]ComData_Clayton SG2_INT[10].13 | 1 | 10.168.100.111 | Booster Pump Failure
15 | [PLC]B3:4.14 | N15:10.14 | [Skynet]ComData_Clayton SG2_INT[10].14 | 1 | 10.168.100.111 | Damper Failure
16 | [PLC]B3:4.15 | N15:10.15 | [Skynet]ComData_Clayton SG2_INT[10].15 | 1 | 10.168.100.111 | Burner Safeguard Tripped
Data# |  |  | Tag name | Value | Path IP | Decription
Inputs
1 | [PLC]I:0.0 | N15:0.0 | [Skynet]ComData_Clayton SG2_INT[0].0 | 1 | 10.168.100.111 | E-Stop Circuit
2 | [PLC]I:0.1 | N15:0.1 | [Skynet]ComData_Clayton SG2_INT[0].1 | 1 | 10.168.100.111 | Start
3 | [PLC]I:0.2 | N15:0.2 | [Skynet]ComData_Clayton SG2_INT[0].2 | 1 | 10.168.100.111 | Limit Pressure Switch
4 | [PLC]I:0.3 | N15:0.3 | [Skynet]ComData_Clayton SG2_INT[0].3 | 1 | 10.168.100.111 | Main Temperature Limit Controller
5 | [PLC]I:0.4 | N15:0.4 | [Skynet]ComData_Clayton SG2_INT[0].4 | 1 | 10.168.100.111 | Auxilliary Thermostat switch
6 | [PLC]I:0.5 | N15:0.5 | [Skynet]ComData_Clayton SG2_INT[0].5 | 1 | 10.168.100.111 | Electronic Safety Control Alarm
7 | [PLC]I:0.6 | N15:0.6 | [Skynet]ComData_Clayton SG2_INT[0].6 | 1 | 10.168.100.111 | Blower
8 | [PLC]I:0.7 | N15:0.7 | [Skynet]ComData_Clayton SG2_INT[0].7 | 1 | 10.168.100.111 | VSD Fault
9 | [PLC]I:0.8 | N15:0.8 | [Skynet]ComData_Clayton SG2_INT[0].8 | 1 | 10.168.100.111 | Motor Overload
10 | [PLC]I:0.9 | N15:0.9 | [Skynet]ComData_Clayton SG2_INT[0].9 | 1 | 10.168.100.111 | Ignition
11 | [PLC]I:0.10 | N15:0.10 | [Skynet]ComData_Clayton SG2_INT[0].10 | 1 | 10.168.100.111 | Stack Damper Limit Switch
12 | [PLC]I:0.11 | N15:0.11 | [Skynet]ComData_Clayton SG2_INT[0].11 | 1 | 10.168.100.111 | Fuel Valves
13 | [PLC]I:0.12 | N15:0.12 | [Skynet]ComData_Clayton SG2_INT[0].12 | 1 | 10.168.100.111 | Pump Oil Level Switch
14 | [PLC]I:0.13 | N15:0.13 | [Skynet]ComData_Clayton SG2_INT[0].13 | 1 | 10.168.100.111 | Spare
15 | [PLC]I:0.14 | N15:0.14 | [Skynet]ComData_Clayton SG2_INT[0].14 | 1 | 10.168.100.111 | Spare
16 | [PLC]I:0.15 | N15:0.15 | [Skynet]ComData_Clayton SG2_INT[0].15 | 1 | 10.168.100.111 | Spare
Outputs
18 | [PLC]O:0.0 | N15:8.0 | [Skynet]ComData_Clayton SG2_INT[8].0 | 1 | 10.168.100.111 | Holding Relay
19 | [PLC]O:0.1 | N15:8.1 | [Skynet]ComData_Clayton SG2_INT[8].1 | 1 | 10.168.100.111 | SPS
20 | [PLC]O:0.2 | N15:8.2 | [Skynet]ComData_Clayton SG2_INT[8].2 | 1 | 10.168.100.111 | Spare
21 | [PLC]O:0.3 | N15:8.3 | [Skynet]ComData_Clayton SG2_INT[8].3 | 1 | 10.168.100.111 | Audible Alarm
22 | [PLC]O:0.4 | N15:8.4 | [Skynet]ComData_Clayton SG2_INT[8].4 | 1 | 10.168.100.111 | VSR Run Relay
23 | [PLC]O:0.5 | N15:8.5 | [Skynet]ComData_Clayton SG2_INT[8].5 | 1 | 10.168.100.111 | Spare
24 | [PLC]O:0.6 | N15:8.6 | [Skynet]ComData_Clayton SG2_INT[8].6 | 1 | 10.168.100.111 | Spare
25 | [PLC]O:0.7 | N15:8.7 | [Skynet]ComData_Clayton SG2_INT[8].7 | 1 | 10.168.100.111 | Stack Damper Relay
26 | [PLC]O:0.8 | N15:8.8 | [Skynet]ComData_Clayton SG2_INT[8].8 | 1 | 10.168.100.111 | Automatic Dump Valve
27 | [PLC]O:0.9 | N15:8.9 | [Skynet]ComData_Clayton SG2_INT[8].9 | 1 | 10.168.100.111 | Makeup Water Valve
28 | [PLC]O:0.10 | N15:8.10 | [Skynet]ComData_Clayton SG2_INT[8].10 | 1 | 10.168.100.111 | Spare
Mode
29 | [PLC]B3:0.1 | N15:9.0 | [Skynet]ComData_Clayton SG2_INT[9].0 | 1 | 10.168.100.111 | Mode Fill / Run
30 | [PLC]B3:1.9 | N15:9.1 | [Skynet]ComData_Clayton SG2_INT[9].1 | 1 | 10.168.100.111 | Mode Auto / Manual
31 | [PLC]B3:2.11 | N15:9.2 | [Skynet]ComData_Clayton SG2_INT[9].2 | 1 | 10.168.100.111 | Mode Primary / Auxilliary
32 |  | N15:9.3 | [Skynet]ComData_Clayton SG2_INT[9].3 | 1 | 10.168.100.111 | Spare
Analog
33 | [PLC]N7:1(*0064) | N16:1 | [Skynet]ComData_Clayton SG2_REAL[1] | Var | 10.168.100.111 | Firing Rate
34 | [PLC]I:1.0 | N15:1 | [Skynet]ComData_Clayton_SG2_INT[1] | Var | 10.168.100.111 | System Steam Pressure
35 | [PLC]I:1.1 | N15:2 | [Skynet]ComData_Clayton_SG2_INT[2] | Var | 10.168.100.111 | Separator Steam Pressure
35 | [PLC]N7:22 | N15:3 | [Skynet]ComData_Clayton SG2_INT[3] | Var | 10.168.100.111 | Op Hours MSR
36 | [PLC]N7:23 | N15:4 | [Skynet]ComData_Clayton SG2_INT[4] | Var | 10.168.100.111 | OP Hours LSR
37 | [PLC]N10:8 | N15:5 | [Skynet]ComData_Clayton SG2_INT[5] | var | 10.168.100.111 | VSD Output %

## Kobelco KNO 60 A (hidden)
Alarm # | Processor OEM Tag | TransferTag | Data Concentrator Tag | Value | Path IP | Message
1 | I:0/0 | N32:0/0 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].0 | 1 | 10.168.100.120 | Oil Pump Motor Overload
2 | I:0/1 | N32:0/1 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].1 | 1 | 10.168.100.120 | Cooling Fan Motor Overload
3 | I:0/2 | N32:0/2 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].2 | 1 | 10.168.100.120 | VFD Faulted
4 | I:0/8 | N32:0/3 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].3 | 1 | 10.168.100.120 | Cabinet Air Temp Limit
5 | I:0/9 | N32:0/4 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].4 | 1 | 10.168.100.120 | High Pressure Limit
6 | I:0/11 | N32:0/5 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].5 | 1 | 10.168.100.120 | Differential Pressure Switch Oil Pressure
7 | O:0/6 | N32:0/6 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].6 | 1 | 10.168.100.120 | Alarm Present
Data# |  |  | Tag name | Value | Path IP | Decription
Status Bits
8 | O:0/2 | N32:0/7 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].7 | 1 | 10.168.100.120 | Standby
9 | O:0/3 | N32:0/8 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].8 | 1 | 10.168.100.120 | Run
10 | O:0/4 | N32:0/9 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].9 | 1 | 10.168.100.120 | Load
11 | O:0/5 | N32:0/10 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].10 | 1 | 10.168.100.120 | Alert
12 | O:0/7 | N32:0/11 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].11 | 1 | 10.168.100.120 | Audible Alarm
13 | O:0/10 | N32:0/12 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].12 | 1 | 10.168.100.120 | Solenoid valve Comp. Load
14 | O:0/0 | N32:0/13 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].13 | 1 | 10.168.100.120 | Oil Pump Running
15 | O:0/1 | N32:0/14 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].14 | 1 | 10.168.100.120 | Cooling Fan Running
16 | O:0/8 | N32:0/15 | [Skynet]ComData_Kobelco_KNO_60A_INT[0].15 | 1 | 10.168.100.120 | Main Drive Running
17 |  | N32:1/0 | [Skynet]ComData_Kobelco_KNO_60A_INT[1].0 | 1 | 10.168.100.120 | Heartbeat
18 |  | N32:1/1 | [Skynet]ComData_Kobelco_KNO_60A_INT[1].1 | 1 | Internal | Comm Loss Bit
19 | O:0/11 | N32:1/2 | [Skynet]ComData_Kobelco_KNO_60A_INT[1].2 | 1 | 10.168.100.120 | Solenoid Valve Interstage Drain
20 | I:0/12 | N32:1/3 | [Skynet]ComData_Kobelco_KNO_60A_INT[1].3 | 1 | 10.168.100.120 | E-Stop Circuit
21 | N11:19 | N32:1/4 | [Skynet]ComData_Kobelco_KNO_60A_INT[1].4 | 1 | 10.168.100.120 | Lead/Lag
Run Time/Counters
22 | F8:0 | N32:2 | [Skynet]ComData_Kobelco_KNO_60A_REAL[2] | Var | 10.168.100.120 | Running Hours
23 | F8:1 | N32:3 | [Skynet]ComData_Kobelco_KNO_60A_REAL[3] | Var | 10.168.100.120 | Loaded Hours
24 | L12:2 | N32:4 | [Skynet]ComData_Kobelco_KNO_60A_REAL[4] | Var | 10.168.100.120 | Load/Unload Cycle Counter
Analog
25 | I3:0 | F33:5 | [Skynet]ComData_Kobelco_KNO_60A_REAL[5] | Var | 10.168.100.120 | Temp Intake Air
26 | I3:1 | F33:6 | [Skynet]ComData_Kobelco_KNO_60A_REAL[6] | Var | 10.168.100.120 | Temp 1st Stage Discharge Air
27 | I3:2 | F33:7 | [Skynet]ComData_Kobelco_KNO_60A_REAL[7] | Var | 10.168.100.120 | Temp 2nd Stage Suction Air
28 | I3:3 | F33:8 | [Skynet]ComData_Kobelco_KNO_60A_REAL[8] | Var | 10.168.100.120 | Temp 2nd Stage Discharge Air
29 | I3:4 | F33:9 | [Skynet]ComData_Kobelco_KNO_60A_REAL[9] | Var | 10.168.100.120 | Temp Aftercooler Outlet
30 | I3:5 | F33:10 | [Skynet]ComData_Kobelco_KNO_60A_REAL[10] | Var | 10.168.100.120 | Temp Lube Oil
31 | F8:7 | F33:11 | [Skynet]ComData_Kobelco_KNO_60A_REAL[11] | Var | 10.168.100.120 | PSI Air Intake
32 | N7:3/100 | F33:12 | [Skynet]ComData_Kobelco_KNO_60A_REAL[12] | Var | 10.168.100.120 | PSI Interstage Air
34 | N7:12/10 | F33:14 | [Skynet]ComData_Kobelco_KNO_60A_REAL[14] | Var | 10.168.100.120 | PSI Lube Oil
35 | N7:1/10 | F33:15 | [Skynet]ComData_Kobelco_KNO_60A_REAL[15] | Var | 10.168.100.120 | PSI System

## Kobelco KNO 60 B (hidden)
Alarm # | Processor OEM Tag | TransferTag | Data Concentrator Tag | Value | Path IP | Message
1 | I:0/0 | N32:0/0 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].0 | 1 | 10.168.100.121 | Oil Pump Motor Overload
2 | I:0/1 | N32:0/1 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].1 | 1 | 10.168.100.121 | Cooling Fan Motor Overload
3 | I:0/2 | N32:0/2 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].2 | 1 | 10.168.100.121 | VFD Faulted
4 | I:0/8 | N32:0/3 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].3 | 1 | 10.168.100.121 | Cabinet Air Temp Limit
5 | I:0/9 | N32:0/4 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].4 | 1 | 10.168.100.121 | High Pressure Limit
6 | I:0/11 | N32:0/5 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].5 | 1 | 10.168.100.121 | Differential Pressure Switch Oil Pressure
7 | O:0/6 | N32:0/6 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].6 | 1 | 10.168.100.121 | Alarm Present
Data# |  |  | Tag name | Value | Path IP | Decription
Status Bits
8 | O:0/2 | N32:0/7 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].7 | 1 | 10.168.100.121 | Standby
9 | O:0/3 | N32:0/8 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].8 | 1 | 10.168.100.121 | Run
10 | O:0/4 | N32:0/9 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].9 | 1 | 10.168.100.121 | Load
11 | O:0/5 | N32:0/10 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].10 | 1 | 10.168.100.121 | Alert
12 | O:0/7 | N32:0/11 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].11 | 1 | 10.168.100.121 | Audible Alarm
13 | O:0/10 | N32:0/12 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].12 | 1 | 10.168.100.121 | Solenoid valve Comp. Load
14 | O:0/0 | N32:0/13 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].13 | 1 | 10.168.100.121 | Oil Pump Running
15 | O:0/1 | N32:0/14 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].14 | 1 | 10.168.100.121 | Cooling Fan Running
16 | O:0/8 | N32:0/15 | [Skynet]ComData_Kobelco_KNO_60B_INT[0].15 | 1 | 10.168.100.121 | Main Drive Running
17 |  | N32:1/0 | [Skynet]ComData_Kobelco_KNO_60B_INT[1].0 | 1 | 10.168.100.121 | Heartbeat
18 |  | N32:1/1 | [Skynet]ComData_Kobelco_KNO_60B_INT[1].1 | 1 | Internal | Comm Loss Bit
19 | O:0/11 | N32:1/2 | [Skynet]ComData_Kobelco_KNO_60B_INT[1].2 | 1 | 10.168.100.121 | Solenoid Valve Interstage Drain
20 | I:0/12 | N32:1/3 | [Skynet]ComData_Kobelco_KNO_60B_INT[1].3 | 1 | 10.168.100.121 | E-Stop Circuit
21 | N11:19 | N32:1/4 | [Skynet]ComData_Kobelco_KNO_60B_INT[1].4 | 1 | 10.168.100.121 | Lead/Lag
Run Time/Counters
22 | F8:0 | N32:2 | [Skynet]ComData_Kobelco_KNO_60B_REAL[2] | Var | 10.168.100.121 | Running Hours
23 | F8:1 | N32:3 | [Skynet]ComData_Kobelco_KNO_60B_REAL[3] | Var | 10.168.100.121 | Loaded Hours
24 | L12:2 | N32:4 | [Skynet]ComData_Kobelco_KNO_60B_REAL[4] | Var | 10.168.100.121 | Load/Unload Cycle Counter
Analog
25 | I3:0 | F33:5 | [Skynet]ComData_Kobelco_KNO_60B_REAL[5] | Var | 10.168.100.121 | Temp Intake Air
26 | I3:1 | F33:6 | [Skynet]ComData_Kobelco_KNO_60B_REAL[6] | Var | 10.168.100.121 | Temp 1st Stage Discharge Air
27 | I3:2 | F33:7 | [Skynet]ComData_Kobelco_KNO_60B_REAL[7] | Var | 10.168.100.121 | Temp 2nd Stage Suction Air
28 | I3:3 | F33:8 | [Skynet]ComData_Kobelco_KNO_60B_REAL[8] | Var | 10.168.100.121 | Temp 2nd Stage Discharge Air
29 | I3:4 | F33:9 | [Skynet]ComData_Kobelco_KNO_60B_REAL[9] | Var | 10.168.100.121 | Temp Aftercooler Outlet
30 | I3:5 | F33:10 | [Skynet]ComData_Kobelco_KNO_60B_REAL[10] | Var | 10.168.100.121 | Temp Lube Oil
31 | F8:7 | F33:11 | [Skynet]ComData_Kobelco_KNO_60B_REAL[11] | Var | 10.168.100.121 | PSI Air Intake
32 | N7:3/100 | F33:12 | [Skynet]ComData_Kobelco_KNO_60B_REAL[12] | Var | 10.168.100.121 | PSI Interstage Air
34 | N7:12/10 | F33:14 | [Skynet]ComData_Kobelco_KNO_60B_REAL[14] | Var | 10.168.100.121 | PSI Lube Oil
35 | N7:1/10 | F33:15 | [Skynet]ComData_Kobelco_KNO_60B_REAL[15] | Var | 10.168.100.121 | PSI System

## Kobelco KNO 200 (hidden)
Alarm # | Processor OEM Tag | TransferTag | Data Concentrator Tag | Value | Path IP | Message
1 | I:0/0 | N32:0/0 | [Skynet]ComData_Kobelco_KNO200_INT[0].0 | 1 | 10.168.100.122 | Oil Pump Motor Overload
2 | I:0/1 | N32:0/1 | [Skynet]ComData_Kobelco_KNO200_INT[0].1 | 1 | 10.168.100.122 | Cooling Fan Motor Overload
3 | I:0/2 | N32:0/2 | [Skynet]ComData_Kobelco_KNO200_INT[0].2 | 1 | 10.168.100.122 | VFD Faulted
4 | I:0/8 | N32:0/3 | [Skynet]ComData_Kobelco_KNO200_INT[0].3 | 1 | 10.168.100.122 | Cabinet Air Temp Limit
5 | I:0/9 | N32:0/4 | [Skynet]ComData_Kobelco_KNO200_INT[0].4 | 1 | 10.168.100.122 | High Pressure Limit
6 | I:0/11 | N32:0/5 | [Skynet]ComData_Kobelco_KNO200_INT[0].5 | 1 | 10.168.100.122 | Differential Pressure Switch Oil Pressure
7 | O:0/6 | N32:0/6 | [Skynet]ComData_Kobelco_KNO200_INT[0].6 | 1 | 10.168.100.122 | Alarm Present
Data# |  |  | Tag name | Value | Path IP | Decription
Status Bits
8 | O:0/2 | N32:0/7 | [Skynet]ComData_Kobelco_KNO200_INT[0].7 | 1 | 10.168.100.120 | Standby
9 | O:0/3 | N32:0/8 | [Skynet]ComData_Kobelco_KNO200_INT[0].8 | 1 | 10.168.100.120 | Run
10 | O:0/4 | N32:0/9 | [Skynet]ComData_Kobelco_KNO200_INT[0].9 | 1 | 10.168.100.120 | Load
11 | O:0/5 | N32:0/10 | [Skynet]ComData_Kobelco_KNO200_INT[0].10 | 1 | 10.168.100.120 | Alert
12 | O:0/7 | N32:0/11 | [Skynet]ComData_Kobelco_KNO200_INT[0].11 | 1 | 10.168.100.120 | Audible Alarm
13 | O:0/10 | N32:0/12 | [Skynet]ComData_Kobelco_KNO200_INT[0].12 | 1 | 10.168.100.120 | Solenoid valve Comp. Load
14 | O:0/0 | N32:0/13 | [Skynet]ComData_Kobelco_KNO200_INT[0].13 | 1 | 10.168.100.120 | Oil Pump Running
15 | O:0/1 | N32:0/14 | [Skynet]ComData_Kobelco_KNO200_INT[0].14 | 1 | 10.168.100.120 | Cooling Fan Running
16 | O:0/8 | N32:0/15 | [Skynet]ComData_Kobelco_KNO200_INT[0].15 | 1 | 10.168.100.120 | Main Drive Running
17 |  | N32:1/0 | [Skynet]ComData_Kobelco_KNO200_INT[1].0 | 1 | 10.168.100.120 | Heartbeat
18 |  |  | [Skynet]ComData_Kobelco_KNO200_INT[1].1 | 1 | Internal | Comm Loss Bit
Run Time/Counters
19 | F8:0 | N32:2 | [Skynet]ComData_Kobelco_KNO200_REAL[2] | Var | 10.168.100.120 | Running Hours
20 | F8:1 | N32:3 | [Skynet]ComData_Kobelco_KNO200_REAL[3] | Var | 10.168.100.120 | Loaded Hours
21 | L12:2 | N32:4 | [Skynet]ComData_Kobelco_KNO200_REAL[4] | Var | 10.168.100.120 | Load/Unload Cycle Counter
Analog
22 | I3:0 | N32:5 | [Skynet]ComData_Kobelco_KNO200_REAL[5] | Var | 10.168.100.120 | Temp Intake Air
23 | I3:1 | N32:6 | [Skynet]ComData_Kobelco_KNO200_REAL[6] | Var | 10.168.100.120 | Temp 1st Stage Discharge Air
24 | I3:2 | N32:7 | [Skynet]ComData_Kobelco_KNO200_REAL[7] | Var | 10.168.100.120 | Temp 2nd Stage Suction Air
25 | I3:3 | N32:8 | [Skynet]ComData_Kobelco_KNO200_REAL[8] | Var | 10.168.100.120 | Temp 2nd Stage Discharge Air
26 | I3:4 | N32:9 | [Skynet]ComData_Kobelco_KNO200_REAL[9] | Var | 10.168.100.120 | Temp Aftercooler Outlet
27 | I3:5 | N32:10 | [Skynet]ComData_Kobelco_KNO200_REAL[10] | Var | 10.168.100.120 | Temp Lube Oil
28 | N7:0 mod | N32:11 | [Skynet]ComData_Kobelco_KNO200_REAL[11] | Var | 10.168.100.120 | PSI Air Intake
29 | N7:69/100 | N32:12 | [Skynet]ComData_Kobelco_KNO200_REAL[12] | Var | 10.168.100.120 | PSI Interstage Air
30 | N7:2/10 | N32:13 | [Skynet]ComData_Kobelco_KNO200_REAL[13] | Var | 10.168.100.120 | PSI 2nd Stage Discharge
31 | N7:3/10 | N32:14 | [Skynet]ComData_Kobelco_KNO200_REAL[14] | Var | 10.168.100.120 | PSI Lube Oil
32 | N11:82/10 | N32:15 | [Skynet]ComData_Kobelco_KNO200_REAL[15] | Var | 10.168.100.120 | PSI System

## Alpha KGM 080
HMI Fault Messages:
Alarm # | Processor OEM Tag | TransferTag | Data Concentrator Tag | Value | Path IP | Message | Python Variable Name
Alpha Cooling Tunnel #1
1 | [KGM080]LskAddFault[0].0 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].0 | 1 | 10.168.100.10 | KK: Emergency stop cooler infeed left hand side (AE2 S7)
2 | [KGM080]LskAddFault[0].1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].1 | 1 | 10.168.100.10 | KK: Emergency stop cooler infeed right hand side (AE2 S8)
3 | [KGM080]LskAddFault[0].2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].2 | 1 | 10.168.100.10 | KK: Emergency stop cooler discharge left hand side (AE2 S9)
4 | [KGM080]LskAddFault[0].3 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].3 | 1 | 10.168.100.10 | KK: Emergency stop cooler discharge right hand side (AE2 S10)
9 | [KGM080]LskAddFault[0].8 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].8 | 1 | 10.168.100.10 | KK: Air pressure belt tension (FD1 B3)
15 | [KGM080]LskAddFault[0].14 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].14 | 1 | 10.168.100.10 | Please press RESET in order to reset emergency stop relais of cooling tunnels
16 | [KGM080]LskAddFault[0].15 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].15 | 1 | 10.168.100.10 | Spare LSKAddFault bit 15
17 | [KGM080]LskAddFault[0].16 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].16 | 1 | 10.168.100.10 | KK: Local isolator blower section 1 (El1 M1)
18 | [KGM080]LskAddFault[0].17 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].17 | 1 | 10.168.100.10 | KK: Local isolator blower section 2 (EL1 M3)
19 | [KGM080]LskAddFault[0].18 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].18 | 1 | 10.168.100.10 | KK: Local isolator water pump section 1+2 (HA1 M1)
20 | [KGM080]LskAddFault[0].19 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].19 | 1 | 10.168.100.10 | KK: Local isolator dehumidifier section 1+2
21 | [KGM080]LskAddFault[0].20 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].20 | 1 | 10.168.100.10 | KK: Local isolator blower section 3
22 | [KGM080]LskAddFault[0].21 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].21 | 1 | 10.168.100.10 | KK: Local isolator blower section 4
23 | [KGM080]LskAddFault[0].22 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].22 | 1 | 10.168.100.10 | KK: Local isolator water pump section 3+4
24 | [KGM080]LskAddFault[0].23 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].23 | 1 | 10.168.100.10 | KK: Local isolator dehumidifier section 3+4
25 | [KGM080]LskAddFault[0].24 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].24 | 1 | 10.168.100.10 | KK: Local isolator belt drive
26 | [KGM080]LskAddFault[0].25 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].25 | 1 | 10.168.100.10 | KK: Wire belt table not plugged in
27 | [KGM080]LskAddFault[0].26 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].26 | 1 | 10.168.100.10 | KK: Local isolator belt wash unit
28 | [KGM080]LskAddFault[0].27 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[5].27 | 1 | 10.168.100.10 | KK: Nut Discharge Conveyor not plugged in
29 | [KGM080]LskAddFault[1].0 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].0 | 1 | 10.168.100.10 | KK: Temperature min alarm air top cooling section 1 (EL1 B1)
30 | [KGM080]LskAddFault[1].1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].1 | 1 | 10.168.100.10 | KK: Temperature min alarm air top cooling section 2 (EL1 B2)
31 | [KGM080]LskAddFault[1].2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].2 | 1 | 10.168.100.10 | KK: Temperature min alarm water bottom cooling section 1+2 (HA1 B1)
37 | [KGM080]LskAddFault[1].8 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].8 | 1 | 10.168.100.10 | KK: Temperature max alarm air top cooling section 1 (EL1 B1)
38 | [KGM080]LskAddFault[1].9 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].9 | 1 | 10.168.100.10 | KK: Temperature max alarm air top cooling section 2 (EL1 B2)
39 | [KGM080]LskAddFault[1].10 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].10 | 1 | 10.168.100.10 | KK: Temperature max alarm water bottom cooling section 1+2 (HA1 B1)
45 | [KGM080]LskAddFault[1].16 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].16 | 1 | 10.168.100.10 | KK: Temperature deviation air top cooling section 1 (EL1 B1)
46 | [KGM080]LskAddFault[1].17 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].17 | 1 | 10.168.100.10 | KK: Temperature deviation air top cooling section 2 (EL1 B2)
47 | [KGM080]LskAddFault[1].18 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[6].18 | 1 | 10.168.100.10 | KK: Temperature deviation water bottom cooling section 1+2 (HA1 B1)
Alpha KGM
61 | [KGM080]KgmAddFault[0].0 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].0 | 1 | 10.168.100.10 | KGM: Fuse block 24VDC (AB1 F2)
62 | [KGM080]KgmAddFault[0].1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].1 | 1 | 10.168.100.10 | KGM: Local isolator water pump (DA1 M1)
63 | [KGM080]KgmAddFault[0].2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].2 | 1 | 10.168.100.10 | KGM: Belt tension belt drive (FD1 B3)
64 | [KGM080]KgmAddFault[0].3 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].3 | 1 | 10.168.100.10 | KGM: Local isolator lift drive (DD1 M1)
65 | [KGM080]KgmAddFault[0].4 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].4 | 1 | 10.168.100.10 | KGM: Thermal contact/plug fill drive NBD 1 (HB1 M1)
66 | [KGM080]KgmAddFault[0].5 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].5 | 1 | 10.168.100.10 | KGM: Thermal contact/plug fill drive NBD 2 (HB1 M2)
67 | [KGM080]KgmAddFault[0].6 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].6 | 1 | 10.168.100.10 | KGM: Local isolator hot air blower SCD (DB1 M1)
68 | [KGM080]KgmAddFault[0].7 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].7 | 1 | 10.168.100.10 | KGM: Thermal protection hot air blower SCD, heater 1 (DB1 E1)
69 | [KGM080]KgmAddFault[0].8 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].8 | 1 | 10.168.100.10 | KGM: Thermal protection hot air blower SCD, heater 2 (DB1 E2)
70 | [KGM080]KgmAddFault[0].9 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].9 | 1 | 10.168.100.10 | KGM: Refill duration of SCD section 1 exceeded (FC3 M2)
71 | [KGM080]KgmAddFault[0].10 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].10 | 1 | 10.168.100.10 | KGM: Refill duration of SCD section 2 exceeded (FC3 M4)
72 | [KGM080]KgmAddFault[0].11 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].11 | 1 | 10.168.100.10 | KGM: Refill duration of SCD section 3 exceeded (FC3 M6)
73 | [KGM080]KgmAddFault[0].12 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].12 | 1 | 10.168.100.10 | NBD 1: No hole detected during init move
74 | [KGM080]KgmAddFault[0].13 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].13 | 1 | 10.168.100.10 | NBD 2: No hole detected during init move
75 | [KGM080]KgmAddFault[0].14 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].14 | 1 | 10.168.100.10 | Spare KGMAddFault bit 14
76 | [KGM080]KgmAddFault[0].15 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].15 | 1 | 10.168.100.10 | KGM: Grease unit empty (AV1 M7)
77 | [KGM080]KgmAddFault[0].16 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].16 | 1 | 10.168.100.10 | KGM: Emergency stop operator panel (AN2 S25)
78 | [KGM080]KgmAddFault[0].17 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].17 | 1 | 10.168.100.10 | KGM: Emergency stop Sollcodrop left hand side (AE2 S1)
79 | [KGM080]KgmAddFault[0].18 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].18 | 1 | 10.168.100.10 | KGM: Emergency stop Sollcodrop right hand side (AE2 S2)
80 | [KGM080]KgmAddFault[0].19 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].19 | 1 | 10.168.100.10 | KGM: Emergency stop KGM discharge left hand side (AE2 S15)
81 | [KGM080]KgmAddFault[0].20 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].20 | 1 | 10.168.100.10 | KGM: Emergency stop KGM discharge right hand side (AE2 S16)
82 | [KGM080]KgmAddFault[0].21 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].21 | 1 | 10.168.100.10 | KGM: Emergency stop NBD infeed left hand side (AE2 S3)
83 | [KGM080]KgmAddFault[0].22 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].22 | 1 | 10.168.100.10 | KGM: Emergency stop NBD infeed right hand side (AE2 S4)
84 | [KGM080]KgmAddFault[0].23 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].23 | 1 | 10.168.100.10 | KGM: Emergency stop NBD discharge left hand side (AE2 S5)
85 | [KGM080]KgmAddFault[0].24 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].24 | 1 | 10.168.100.10 | KGM: Emergency stop NBD discharge right hand side (AE2 S6)
86 | [KGM080]KgmAddFault[0].25 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].25 | 1 | 10.168.100.10 | KGM: Emergency stop KGM infeed left hand side (AE2 S13)
87 | [KGM080]KgmAddFault[0].26 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].26 | 1 | 10.168.100.10 | KGM: Emergency stop KGM infeed right hand side (AE2 S14)
90 | [KGM080]KgmAddFault[0].29 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].29 | 1 | 10.168.100.10 | Enrober 1; Emergency stop in that area
91 | [KGM080]KgmAddFault[0].30 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].30 | 1 | 10.168.100.10 | Enrober 2: Emergency stop in that area
92 | [KGM080]KgmAddFault[0].31 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[0].31 | 1 | 10.168.100.10 | Please press reset in order to switch on Estop relais
93 | [KGM080]KGMAddFault[1].0 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].0 | 1 | 10.168.100.10 | KGM: Temperature min alarm - water heating hopper 1 (DA1 B1)
94 | [KGM080]KGMAddFault[1].1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].1 | 1 | 10.168.100.10 | KGM: Temperature min alarm - Sollcodrop interior (DB1 B1)
101 | [KGM080]KGMAddFault[1].8 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].8 | 1 | 10.168.100.10 | KGM: Temperature max alarm - water heating hopper 1 (DA1 B1)
102 | [KGM080]KGMAddFault[1].9 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].9 | 1 | 10.168.100.10 | KGM: Temperature max alarm - Sollcodrop interior (DB1 B1)
109 | [KGM080]KGMAddFault[1].16 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].16 | 1 | 10.168.100.10 | KGM: Temperature deviation alarm - water heating hopper 1 (DA1 B1)
110 | [KGM080]KGMAddFault[1].17 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].17 | 1 | 10.168.100.10 | KGM: Temperature deviation alarm - Sollcodrop interior (DB1 B1)
117 | [KGM080]KGMAddFault[1].24 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].24 | 1 | 10.168.100.10 | MLC status: Warning
118 | [KGM080]KGMAddFault[1].25 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].25 | 1 | 10.168.100.10 | MLC status: Error
119 | [KGM080]KGMAddFault[1].26 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].26 | 1 | 10.168.100.10 | MLC status: Axis warning
120 | [KGM080]KGMAddFault[1].27 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].27 | 1 | 10.168.100.10 | MLC status: Axis error
121 | [KGM080]KGMAddFault[1].28 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].28 | 1 | 10.168.100.10 | MLC status: Line velocity setpoint too high
122 | [KGM080]KGMAddFault[1].29 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].29 | 1 | 10.168.100.10 | MLC status: Stroke of KGM follower axis too high
123 | [KGM080]KGMAddFault[1].30 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].30 | 1 | 10.168.100.10 | MLC status: Line velocity limit reached
124 | [KGM080]KGMAddFault[1].31 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[1].31 | 1 | 10.168.100.10 | Mlc status: Stroke of Sandwicher follower axis too high
141 | [KGM080]KGMAddFault[2].16 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[2].16 | 1 | 10.168.100.10 | KGM: Ethernet communication to Enrober 1
142 | [KGM080]KGMAddFault[2].17 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[2].17 | 1 | 10.168.100.10 | KGM: Ethernet communication to Turbotemper
156 | [KGM080]KGMAddFault[2].31 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[2].31 | 1 | 10.168.100.10 | KGM: Ethernet communication to TT failed
157 | [KGM080]KGM:Fault.Tempering |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].0 | 1 | 10.168.100.10 | KGM: Tempering
158 | [KGM080]KGM:Fault.Enable |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].1 | 1 | 10.168.100.10 | KGM: Enable
159 | [KGM080]KGM:Fault.KgLiftDrive |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].4 | 1 | 10.168.100.10 | KGM: Lift drive (DD1 M1)
160 | [KGM080]KGM:Fault.KgPiston1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].8 | 1 | 10.168.100.10 | KGM
161 | [KGM080]KGM:Fault.KgPiston1WashMode |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].10 | 1 | 10.168.100.10 | KGM: Wash mode
162 | [KGM080]KGM:Fault.KgFotocellMode |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].12 | 1 | 10.168.100.10 | KGM: Fotocell Mode
163 | [KGM080]KGM:Fault.WaterPumpHopper1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].2 | 1 | 10.168.100.10 | KGM: Water pump hopper (DA1 M1)
164 | [KGM080]KGM:Fault.KgHopper1Refill |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].5 | 1 | 10.168.100.10 | KGM: Hopper refill
165 | [KGM080]KGM:Fault.ScdRefill |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].14 | 1 | 10.168.100.10 | KGM: Refill SCD
166 | [KGM080]KGM:Fault.ScdLights |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].15 | 1 | 10.168.100.10 | KGM: Machine lights SCD (DC1 E1)
167 | [KGM080]KGM:Fault.Nbd1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].16 | 1 | 10.168.100.10 | KGM: NBD 1
168 | [KGM080]KGM:Fault.Nbd1FillDrive |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].17 | 1 | 10.168.100.10 | KGM: NBD 1 fill drive (HB1 M1)
169 | [KGM080]KGM:Fault.Nbd2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].18 | 1 | 10.168.100.10 | KGM: NBD 2
170 | [KGM080]KGM:Fault.Nbd2FillDrive |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].19 | 1 | 10.168.100.10 | KGM: NBD 2 fill drive (HB1 M2)
171 | [KGM080]KGM:Fault.NbdRefill |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].20 | 1 | 10.168.100.10 | KGM: NBD refill
172 | [KGM080]KGM:Fault.NbdFollower |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].21 | 1 | 10.168.100.10 | KGM: NBD follower
173 | [KGM080]KGM:Fault.NbdPusher |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].22 | 1 | 10.168.100.10 | KGM: NBD pusher
174 | [KGM080]KGM:Fault.BeltDrive |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].24 | 1 | 10.168.100.10 | KGM: Belt drive (FB1 M1)
Alpha LSK1 (Cooling Tunnel #1)
175 | [KGM080]Tunnel:Fault.Lsk1BlowerSection1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].1 | 1 | 10.168.100.10 | KK: Blower section 1 (EL1 M1)
176 | [KGM080]Tunnel:Fault.Lsk1BlowerSection2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].2 | 1 | 10.168.100.10 | KK: Blower section 2 (EL1 M2)
177 | [KGM080]Tunnel:Fault.Lsk1WaterPumpSection1u2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].3 | 1 | 10.168.100.10 | KK: Water pump section 1+2 (HA1 M1)
178 | [KGM080]Tunnel:Fault.Lsk1AirDryerSection1u2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].4 | 1 | 10.168.100.10 | KK: Air dryer section 1+2
179 | [KGM080]Tunnel:Fault.Lsk1BlowerSection3 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].5 | 1 | 10.168.100.10 | KK: Blower section 3
180 | [KGM080]Tunnel:Fault.Lsk1BlowerSection4 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].6 | 1 | 10.168.100.10 | KK: Blower section 4
181 | [KGM080]Tunnel:Fault.Lsk1WaterPumpSection3u4 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].7 | 1 | 10.168.100.10 | KK: Water pump section 3+4
182 | [KGM080]Tunnel:Fault.Lsk1AirDryerSection3u4 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].8 | 1 | 10.168.100.10 | KK: AIr dryer section 3+4
183 | [KGM080]Tunnel:Fault.Lsk1Beltdrive |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].9 | 1 | 10.168.100.10 | KK: Belt drive
184 | [KGM080]Tunnel:Fault.Lsk1BeltWash |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].10 | 1 | 10.168.100.10 | KK: Belt wash (FE1 M1)
185 | [KGM080]Tunnel:Fault.Lsk1BeltTempering |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].11 | 1 | 10.168.100.10 | KK: Belt tempering (FH1 E1)
186 | [KGM080]Tunnel:Fault.wireBeltDrive |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].16 | 1 | 10.168.100.10 | KK: Wire belt drive (CE 1M1)
187 | [KGM080]Tunnel:Fault.BlowOffDevice |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].17 | 1 | 10.168.100.10 | KK: Blow off device (CB1 M1)
Alpha KGM
188 | [KGM080]Kgm:Fault.ScdHotAirBlower |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[3].13 | 1 | 10.168.100.10 | KGM: Hot air blower SCD (DB1 M1)
Alpha LSK1 (Cooling Tunnel #1)
189 | [KGM080]LskAddFault[2].0 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[7].0 | 1 | 10.168.100.10 | KK: No communication to belt tempering unit (FH1 E1)
190 | [KGM080]LskAddFault[2].1 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[7].1 | 1 | 10.168.100.10 | KK: Water fill level belt tempering unit (FH1 E1)
191 | [KGM080]LskAddFault[2].2 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[7].2 | 1 | 10.168.100.10 | KK: Temperature probe fault belt tempering unit (FH1 E1)
192 | [KGM080]LskAddFault[2].3 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[7].3 | 1 | 10.168.100.10 | KK: Safety thermostat belt tempering unit (FH1 E1)
193 | [KGM080]LskAddFault[2].4 |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[7].4 | 1 | 10.168.100.10 | KK: Water pump belt tempering unit (FH1 E1)
Alpha KGM
194 | [KGM080]KGM:Fault.ScdValveBypass |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[4].0 | 1 | 10.168.100.10 | KGM: Bypass valve SCD (FC2 M3)
195 | [KGM080]KGM:Fault.ScdFeedValve |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[4].1 | 1 | 10.168.100.10 | KGM: Feed valve SCD (FC2 M4)
196 | [KGM080]KGM:Fault.ScdReturnValve |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[4].2 | 1 | 10.168.100.10 | KGM: Return valve SCD (FC2 M6)
Alpha LSK1 (Cooling Tunnel #1)
240 | [KGM080]Tunnel:Fault.TransferRoller |  | [Skynet]ComData_KGM_080_Alpha_To Skynet.Fault_Data[8].18 | 1 | 10.168.100.10 | KK: Transfer roller (FK1 M1)
Controller Data:
Data# |  |  | Tag name | Value | Path IP | Description | Python Variable Name
1 | [KGM080]RunningProgram |  | ComData_KGM_080_Alpha_To_Skynet.Parameters[0] | Var | 10.168.100.10 | Selected Recipe | kgm_080_selected_recipe
3 | [KGM080]AlarmPresent |  | ComData_KGM_080_Alpha_To_Skynet.Status_Bits[0].0 | 1 | 10.168.100.10 | Fault Present
4 | [KGM080]Fb.ScdValveFeedANDFb.BeltDriveANDFb.Nbd1ANDFb.Nbd2ANDFb.KgPiston1 |  | ComData_KGM_080_Alpha_To_Skynet.Status_Bits[0].1 | 1 | 10.168.100.10 | Production Active @ Line Speed
8 | [Skynet]ComData_KGM_080_Alpha_to Skynet.Status_Bits[22] |  | ComData_KGM_080_Alpha_To_Skynet.Status_Bits[22] | Var | 10.168.100.10 | Buffer Fill Level From Packaging
9 | [KGM080]ComData_KGM_080_Alpha_toSkynet.Counter[0].ACC*2 |  | ComData_KGM_080_Alpha_To_Skynet.Status_Bits[1] | Var | 10.168.100.10 | Produced rows 1999998 reset
10 | [KGM080]ComData_KGM_080_Alpha_toSkynet.Counter[1].ACC*2 |  | ComData_KGM_080_Alpha_To_Skynet.Status_Bits[2] | Var | 10.168.100.10 | Good Rows Produced | kgm_080_good_rows_produced_this_shift
11 | Process Values
12 | [KGM080]Tunnel:ActData.Temp.Lsk1WaterSection1u2 |  | ComData_KGM_080_Alpha_To_Skynet.Process_Values[0] | Var | 10.168.100.10 | Actual Temperature Cooling Water | kgm_080_actual_temperature_cooling_water
13 | [KGM080]Tunnel:ActData.Temp.Lsk1AirSection1 |  | ComData_KGM_080_Alpha_To_Skynet.Process_Values[1] | Var | 10.168.100.10 | Actual Temperature Cooling Tunnel 1 Section 1 | kgm_080_actual_temperature_cooling_tunnel1_section1
14 | [KGM080]Tunnel:ActData.Temp.Lsk1AirSection2 |  | ComData_KGM_080_Alpha_To_Skynet.Process_Values[2] | Var | 10.168.100.10 | Actual Temperature Cooling Tunnel 1 Section 2 | kgm_080_actual_temperature_cooling_tunnel1_section2
15 | [KGM080]Tunnel:ActData.Temp.Lsk1BeltTempering |  | ComData_KGM_080_Alpha_To_Skynet.Process_Values[3] | Var | 10.168.100.10 | Actual Temperature Belt | kgm_080_actual_temperature_belt
23 | [KGM080]KGM:ActData.Temp.ScdInterior |  | ComData_KGM_080_Alpha_To_Skynet.Process_Values[11] | Var | 10.168.100.10 | Actual Temperature Drum Room | kgm_080_actual_temp_drum_room
25 | [KGM080]KGM:ActData.Temp.Hopper1 |  | ComData_KGM_080_Alpha_To_Skynet.Process_Values[13] | Var | 10.168.100.10 | Actual Temperature Depositor | kgm_080_actual_temp_depositor
41 | Setpoint Values
Lsk
42 | [KGM080]Tunnel:Setpoints.Temp.LskAirSection1 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[1] | Var | 10.168.100.10 | Setpoint Temperature Cooling Tunnel 1 Section 1 | kgm_080_setpoint_temperature_cooling_tunnel1_section1
43 | [KGM080]Tunnel:Setpoints.Temp.LskAirSection2 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[2] | Var | 10.168.100.10 | Setpoint Temperature Cooling Tunnel 1 Section 2 | kgm_080_setpoint_temperature_cooling_tunnel1_section2
44 | [KGM080]Tunnel:Setpoints.Speeds.Lsk1BlowerSection1 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[3] | Var | 10.168.100.10 | Setpoint Speed Lsk1 Fan 1 | kgm_080_setpoint_speed_lsk1_fan_1
45 | [KGM080]Tunnel:Setpoints.Speeds.Lsk1BlowerSection2 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[4] | Var | 10.168.100.10 | Setpoint Speed Lsk1 Fan 2 | kgm_080_setpoint_speed_lsk1_fan_2
48 | [KGM080]Tunnel:Setpoints.Temp.Lsk1WaterSection1u2 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[7] | Var | 10.168.100.10 | Setpoint Temperature Cooling Water | kgm_080_setpoint_temperature_cooling_water
49 | [KGM080]Tunnel:setpoints.Temp.Lsk1BeltTempering |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[8] | Var | 10.168.100.10 | Setpoint Belt Temperature | kgm_080_setpoint_belt_temperature
50 | [KGM080]Tunnel:Setpoints.Speeds.WireBeltDrive |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[9] | Var | 10.168.100.10 | Setpoint Speed Wire Belt Section | kgm_080_setpoint_speed_wirebelt_section
51 | [KGM080]Tunnel:Setpoints.Speeds.TransferRoller |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[10] | Var | 10.168.100.10 | Setpoint Speed Spooler | kgm_080_setpoint_speed_spooler
KGM
53 | [KGM080]KGM:Setpoints.Motion.System.Transfervelocity |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[12] | Var | 10.168.100.10 | Transfer Velocity
54 | [KGM080]KGM:Setpoints.Motion.System.LineSpeed |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[13] | Var | 10.168.100.10 | Line Speed (Rows/Min) | kgm_080_line_speed_rows_min
55 | [KGM080]KGM:Setpoins.Temp.Hopper1 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[14] | Var | 10.168.100.10 | Caramel Hopper Temperature | kgm_080_caramel_hopper_temp
56 | [KGM080]KGM:Setpoints.Temp.ScdInterior |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[15] | Var | 10.168.100.10 | Drum Room Temperature | kgm_080_drum_room_temp
57 | [KGM080]KGM:Setpoins.Temp.ChocHoseHeating Scd |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[16] | Var | 10.168.100.10 | Drum Hose Temperature Setpoint | kgm_080_drum_hose_temp_setpoint
58 | [KGM080]KGM:Setpoins.Temp.ChocHoseHeatingKgm |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[17] | Var | 10.168.100.10 | Depositor Hose Setpoint | kgm_080_depositor_hose_setpoint
59 | [KGM080]KGM:Setpoints.Motion.KgmP1.K1 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[18] | Var | 10.168.100.10 | Kv1 | kgm_080_kv1
60 | [KGM080]KGM:Setpoints.Motion.KgmP1.K2 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[19] | Var | 10.168.100.10 | Kv2 | kgm_080_kv2
61 | [KGM080]KGM:Setpoints.Motion.KgmP1.K3 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[20] | Var | 10.168.100.10 | Kv3 | kgm_080_kv3
62 | [KGM080]KGM:Setpoints.Motion.KgmP1.K4 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[21] | Var | 10.168.100.10 | Kv4 | kgm_080_kv4
63 | [KGM080]KGM:Setpoints.Motion.KgmP1.K5 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[22] | Var | 10.168.100.10 | Kv5 | kgm_080_kv5
64 | [KGM080]KGM:Setpoints.Motion.KgmP1.Phase |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[23] | Var | 10.168.100.10 | Delay | kgm_080_delay
65 | [KGM080]KGM:Setpoints.Motion.KgmP1.DepositonVolume |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[24] | Var | 10.168.100.10 | Depositor Volume | kgm_080_depositior_volume
66 | [KGM080]KGM:Setpoints.Motion.KgmP1.DepositionDuration |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[25] | Var | 10.168.100.10 | Depositor Duration | kgm_080_depositor_duration
67 | [KGM080]KGM:Setpoints.Motion.KgmP1.PullbackStroke |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[26] | Var | 10.168.100.10 | Pull Up Stroke | kgm_080_pull_up_stroke
68 | [KGM080]KGM:Setpoints.Motion.KgmP1.LoadDuration |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[27] | Var | 10.168.100.10 | Load Duration | kgm_080_load_duration
69 | [KGM080]KGM:Setpoints.Motion.KgmMaster.Phase |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[28] | Var | 10.168.100.10 | KGM Delay | kgm_080_kgm_delay
70 | [KGM080]KGM:Setpoints.Motion.KgmF.Phase |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[29] | Var | 10.168.100.10 | Delay
71 | [KGM080]KGM:Setpoints.Motion.KgmF.IdleRange |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[30] | Var | 10.168.100.10 | Idle Range | kgm_080_idle_range
72 | [KGM080]KGM:Setpoints.Motion.KgmF.FollowerDistance |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[31] | Var | 10.168.100.10 | Sync Distance | kgm_080_sync_distance
73 | [KGM080]KGM:Setpoints.Motion.KgmF.SpeedFactor |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[32] | Var | 10.168.100.10 | Speed Factor | kgm_080_speed_factor
NBD
75 | [KGM080]KGM:Setpoints.Motion.Nbd.MachinePhase |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[34] | Var | 10.168.100.10 | Delay
76 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum1Phase |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[35] | Var | 10.168.100.10 | Drum 1 Delay | kgm_080_drum_1_delay
77 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum2Phase |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[36] | Var | 10.168.100.10 | Drum 2 Delay | kgm_080_drum_2_delay
78 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum1StartAngle |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[37] | Var | 10.168.100.10 | Drum 1 Start Angle | kgm_080_drum_1_start_angle
79 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum2StartAngle |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[38] | Var | 10.168.100.10 | Drum 2 Start Angle | kgm_080_drum_2_start_angle
80 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum1ForwardMoveRange |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[39] | Var | 10.168.100.10 | Drum 1 Forward Move Range | kgm_080_drum_1_forward_move_range
81 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum2ForwardMoveRange |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[40] | Var | 10.168.100.10 | Drum 2 Forward Move Range | kgm_080_drum_2_forward_move_range
82 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum1ReverseMoveRange |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[41] | Var | 10.168.100.10 | Drum 1 Reverse Move Range | kgm_080_drum_1_reverse_move_range
83 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum2ReverseMoveRange |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[42] | Var | 10.168.100.10 | Drum 2 Reverse Move Range | kgm_080_drum_2_reverse_move_range
84 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum1ReverseAngle |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[43] | Var | 10.168.100.10 | Drum 1 Reverse Angle | kgm_080_drum_1_reverse_angle
85 | [KGM080]KGM:Setpoints.Motion.Nbd.Drum2ReverseAngle |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[44] | Var | 10.168.100.10 | Drum 2 Reverse Angle | kgm_080_drum_2_reverse_angle
86 | [KGM080]KGM:Setpoints.Motion.Nbd.FollowerDistance |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[45] | Var | 10.168.100.10 | Follower Travel Distance | kgm_080_follower_travel_distance
87 | [KGM080]KGM:Setpoints.Speeds.Nbd1FillDrive |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[46] | Var | 10.168.100.10 | Drum 1 Fill Drive | kgm_080_drum_1_fill_drive
88 | [KGM080]KGM:Setpoints.Speeds.Nbd2FillDrive |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[47] | Var | 10.168.100.10 | Drum 2 Fill Drive | kgm_080_drum_2_fill_drive
89 | [KGM080]KGM:Setpoints.Motion.IntervalNbdRake2 |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[48] | Var | 10.168.100.10 | Rake Interval | kgm_080_rake_interval
90 | [KGM080]KGM:Setpoints.Motion.Nbd.FollowerPosPusherDown |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[49] | Var | 10.168.100.10 | Pusher Down | kgm_080_pusher_down
91 | [KGM080]KGM:Setpoints.Motion.Nbd.FollowerPosPusherUp |  | ComData_KGM_080_Alpha_To_Skynet.Setpoint_Values[50] | Var | 10.168.100.10 | Pusher Up | kgm_080_pusher_up

## Alpha TTB 015
HMI Fault Messages:
Alarm # | Processor OEM Tag | Data Concentrator Tag | Value | Path IP | Message | Python Variable Name
Alpha TT400 (Tempering1)
1 | [TTB015]TcAddFault[0].0 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].0 | 1 | 10.168.100.10 | Temperature low
2 | [TTB015]TcAddFault[0].1 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].1 | 1 | 10.168.100.10 | High Chocolate Pressure
3 | [TTB015]TcAddFault[0].2 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].2 | 1 | 10.168.100.10 | Chocolate path at SCD valves not clear
4 | [TTB015]TcAddFault[0].3 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].3 | 1 | 10.168.100.10 | Thermistor scraper
5 | [TTB015]TcAddFault[0].4 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].4 | 1 | 10.168.100.10 | Local isolator feed pump
6 | [TTB015]TcAddFault[0].5 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].5 | 1 | 10.168.100.10 | Chocolate pipe not clear
7 | [TTB015]TcAddFault[0].6 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].6 | 1 | 10.168.100.10 | Scraper drive switch off due to feed pump stop
8 | [TTB015]TcAddFault[0].7 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].7 | 1 | 10.168.100.10 | Fuse block control voltage 24VDC
9 | [TTB015]TcAddFault[0].8 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].8 | 1 | 10.168.100.10 | Chocolate level max max
10 | [TTB015]TcAddFault[0].9 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[1].9 | 1 | 10.168.100.10 | Chocolate level below min
11 | [TTB015]TcAddFault[1].0 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].0 | 1 | 10.168.100.10 | Temperature min alarm heating stage
12 | [TTB015]TcAddFault[1].1 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].1 | 1 | 10.168.100.10 | Temperature min alarm water cooling stage
13 | [TTB015]TcAddFault[1].2 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].2 | 1 | 10.168.100.10 | Temperature min alarm chocolate cooling stage
14 | [TTB015]TcAddFault[1].3 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].3 | 1 | 10.168.100.10 | Temperature min alarm water mixing stage
15 | [TTB015]TcAddFault[1].4 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].4 | 1 | 10.168.100.10 | Temperature min alarm water pipe
16 | [TTB015]TcAddFault[1].5 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].5 | 1 | 10.168.100.10 | Drive16
17 | [TTB015]TcAddFault[1].8 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].8 | 1 | 10.168.100.10 | Temperature max alarm heating stage
18 | [TTB015]TcAddFault[1].9 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].9 | 1 | 10.168.100.10 | Temperature max alarm water cooling stage
19 | [TTB015]TcAddFault[1].10 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].10 | 1 | 10.168.100.10 | Temperature max alarm chocolate cooling stage
20 | [TTB015]TcAddFault[1].11 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].11 | 1 | 10.168.100.10 | Temperature max alarm water mixing stage
21 | [TTB015]TcAddFault[1].12 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].12 | 1 | 10.168.100.10 | Temperature max alarm water pipe
22 | [TTB015]TcAddFault[1].13 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].13 | 1 | 10.168.100.10 | Drive22
23 | [TTB015]TcAddFault[1].16 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].16 | 1 | 10.168.100.10 | Temperature deviation heating stage
24 | [TTB015]TcAddFault[1].17 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].17 | 1 | 10.168.100.10 | Temperature deviation water cooling stage
25 | [TTB015]TcAddFault[1].18 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].18 | 1 | 10.168.100.10 | Temperature deviation chocolate cooling stage
26 | [TTB015]TcAddFault[1].19 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].19 | 1 | 10.168.100.10 | Temperature min alarm water mixing stage
27 | [TTB015]TcAddFault[1].20 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].20 | 1 | 10.168.100.10 | Temperature min alarm water pipe
28 | [TTB015]TcAddFault[1].21 | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[2].21 | 1 | 10.168.100.10 | add flt 1-21
29 | [TTB015]Tempering:Fault.WaterPumpCST | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[9].3 | 1 | 10.168.100.10 | Water pump cooling stage
30 | [TTB015]Tempering:Fault.WaterPumpHST | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[9].2 | 1 | 10.168.100.10 | Water pump heating stage
31 | [TTB015]Tempering:Fault.WaterPumpMST | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[9].4 | 1 | 10.168.100.10 | Water pump mixing stage
32 | [TTB015]Tempering:Fault.WaterPumpPipe | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[9].5 | 1 | 10.168.100.10 | Water pump chocolate pipe
33 | [TTB015]Tempering:Fault.FeedPump | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[9].7 | 1 | 10.168.100.10 | Feed pump
34 | [TTB015]Tempering:Fault.Scraper | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[9].6 | 1 | 10.168.100.10 | Scraper drive
35 | [TTB015]Tempering:Fault.Stirrer | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Fault_Data[9].9 | 1 | 10.168.100.10 | Stirrer
Controller Data:
Data# |  | Tag name | Value | Path IP | Description | Python Variable Name
Status Bits
1 | [TTB015]Tempering:AlarmPresent | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Status_Bits[0].0 | 1 | 10.168.100.10 | Fault Present
2 | [TTB015]Tempering:Fb.Tempering | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Status_Bits[0].1 | 1 | 10.168.100.10 | Running
Parameters
3 | [TTB015]Tempering:RunningProgram | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Parameters[0] | Var | 10.168.100.10 | Selected Program | ttb_015_selected_program
Process Values
4 | [TTB015]Tempering:ActData.Temp.ChocolateInfeed | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[0] | Var | 10.168.100.10 | Actual Temperature Chocolate Infeed | ttb_015_actual_temp_chocolate_infeed
5 | [TTB015]Tempering:ActData.Temp.HeatingStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[1] | Var | 10.168.100.10 | Actual Temperature Heating Stage | ttb_015_actual_temp_heating_stage
6 | [TTB015]Tempering:ActData.Temp.WaterHeatStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[2] | Var | 10.168.100.10 | Actual Temperature Water Heat Stage | ttb_015_actual_temp_water_heat_stage
7 | [TTB015]Tempering:ActData.Temp.ChocHeatStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[3] | Var | 10.168.100.10 | Actual Temperature Chocolate Heat Stage | ttb_015_actual_temp_chocolate_heat_stage
8 | [TTB015]Tempering:ActData.Temp.WaterCoolStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[4] | Var | 10.168.100.10 | Actual Temperature Water Cool Stage | ttb_015_actual_temp_water_cool_stage_
9 | [TTB015]Tempering:ActData.Temp.ChocCoolStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[5] | Var | 10.168.100.10 | Actual Temperature Chocolate Cool Stage | ttb_015_actual_temp_choc_cool_stage
10 | [TTB015]Tempering:ActData.Temp.WaterMixStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[6] | Var | 10.168.100.10 | Actual Temperature Water Mix Stage | ttb_015_actual_temp_water_mix_stage
11 | [TTB015]Tempering:ActData.Temp.ChocMixstage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[7] | Var | 10.168.100.10 | Actual Temperature Chocolate Mix Stage | ttb_015_actual_temp_choc_mix_stage
12 | [TTB015]Tempering:ActData.Temp.WaterChocPipe | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[8] | Var | 10.168.100.10 | Actual Temperature Water Chocolate Pipe | ttb_015_actual_temp_water_choc_pipe
31 | [TTB015]Tempering:ActData.Data.ChocPressure | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[9] | Var | 10.168.100.10 | Actual Pump Discharge Pressure | ttb_015_actual_pump_discharge_pressure
32 | [TTB015]Tempering:ActData.Data.Tank Level | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Process_Values[10] | Var | 10.168.100.10 | Actual Tank Level | ttb_015_actual_tank_level
Setpoint Values
33 | [TTB015]Tempering:Setpoints.Temp.ChocolateInfeed | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[0] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Infeed | ttb_015_setpoint_temp_chocolate_infeed
34 | [TTB015]Tempering:Setpoints.Temp.HeatingStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[1] | Var | 10.168.100.10 | Setpoint Temperature Heating Stage | ttb_015_setpoint_temp_heating_stage
35 | [TTB015]Tempering:Setpoints.Temp.WaterHeatStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[2] | Var | 10.168.100.10 | Setpoint Temperature Water Heat Stage | ttb_015_setpoint_temp_water_heat_stage
36 | [TTB015]Tempering:Setpoints.Temp.ChocHeatStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[3] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Heat Stage | ttb_015_setpoint_temp_chocolate_heat_stage
37 | [TTB015]Tempering:Setpoints.Temp.WaterCoolStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[4] | Var | 10.168.100.10 | Setpoint Temperature Water Cool Stage | ttb_015_setpoint_temp_water_cool_stage
38 | [TTB015]Tempering:Setpoints.Temp.ChocCoolStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[5] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Cool Stage | ttb_015_setpoint_temp_choc_cool_stage
39 | [TTB015]Tempering:Setpoints.Temp.WaterMixStage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[6] | Var | 10.168.100.10 | Setpoint Temperature Water Mix Stage | ttb_015_setpoint_temp_water_mix_stage
40 | [TTB015]Tempering:Setpoints.Temp.ChocMixstage | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[7] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Mix Stage | ttb_015_setpoint_temp_choc_mix_stage
41 | [TTB015]Tempering:Setpoints.Temp.WaterChocPipe | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[8] | Var | 10.168.100.10 | Setpoint Temperature Water Chocolate Pipe | ttb_015_setpoint_temp_water_choc_pipe
42 | [TTB015]Tempering:Setpoints.Speeds.FeedPump | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[9] | Var | 10.168.100.10 | Setpoint Feed Pump (kg/hr) | ttb_015_setpoint_feed_pump_kg_hr
43 | [TTB015]Tempering:Settings.Tank.Level_StartRefill | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[10] | Var | 10.168.100.10 | Setpoint to Start Refill | ttb_015_setpoint_to_start_refill
44 | [TTB015]Tempering:Settings.Tank.Level_StopRefill | [Skynet]ComData_TTB_015_Alpha_To_Skynet.Setpoint_Values[11] | Var | 10.168.100.10 | Setpoint to Stop Refill | ttb_015_setpoint_to_stop_refill

## Alpha M5 090
HMI Fault Messages:
Alarm # | Processor OEM Tag | Data Concentrator Tag | Value | Path IP | Message
M5 090 Enrober
1 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].0 | 1 | 10.168.100.11 | M5: Low start temperature
2 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].1 | 2 | 10.168.100.11 | M5: Service cover sump open
4 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].3 | 4 | 10.168.100.11 | M5: Air pressure wire belt
5 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].4 | 5 | 10.168.100.11 | M5: Wire belt tension operator side fully extended (CE1 B7)
6 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].5 | 6 | 10.168.100.11 | M5: Wire belt tension operator side fully contracted (CE1 B6)
7 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].6 | 7 | 10.168.100.11 | M5: Wire belt tension drive side fully extended (CE1 B4)
8 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].7 | 8 | 10.168.100.11 | M5: Wire belt tension drive side fully contracted (CE1 B3)
9 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].8 | 9 | 10.168.100.11 | M5: Chocolate valve in front of return pump closed (CH1 S2))
10 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].9 | 10 | 10.168.100.11 | M5: Chocolate valve behind return pump closed (CH1 S3)
11 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].10 | 11 | 10.168.100.11 | M5: Chocolate return path not clear
12 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].11 | 12 | 10.168.100.11 | M5: Local isolator return pump (CH1 M1)
13 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].12 | 13 | 10.168.100.11 | M5: Curtain roller not plugged in
14 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].13 | 14 | 10.168.100.11 | M5: Fuse block 24VDC
15 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].14 | 15 | 10.168.100.11 | M5: Detailer not plugged in (CX1 M1)
17 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].16 | 17 | 10.168.100.11 | M5: Emergency stop left hand side (AE1 S3)
18 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].17 | 18 | 10.168.100.11 | M5: Emergency stop right hand side (AE1 S4)
22 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].21 | 22 | 10.168.100.11 | KGM: Emergency stop in that area
23 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].22 | 23 | 10.168.100.11 | M5 2: Emergency stop in that area
24 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].23 | 24 | 10.168.100.11 | Please press reset i.o. to reset Estop relay
29 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].28 | 29 | 10.168.100.11 | M5: PointIO communication to cooling tunnel cabinet failed
30 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].29 | 30 | 10.168.100.11 | M5: Ethernet communication to KGM
31 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].30 | 31 | 10.168.100.11 | M5: Ethernet communication to M5 2
32 | [M5090]Program:Enrober.Fault.M5AddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[0].31 | 32 | 10.168.100.11 | M5: Ethernet communication to TT
33 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].0 | 1 | 10.168.100.11 | LSK: Min Alarm - Water sump (DA1 B1)
34 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].1 | 2 | 10.168.100.11 | LSK: Min Alarm - Water table (DA1 B2)
35 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].2 | 3 | 10.168.100.11 | LSK: Min alarm - Machine interior (DB1 B1)
41 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].8 | 9 | 10.168.100.11 | LSK: Max Alarm - Water sump (DA1 B1)
42 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].9 | 10 | 10.168.100.11 | LSK: Max Alarm - Water table (DA1 B2)
43 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].10 | 11 | 10.168.100.11 | LSK: Max Alarm - Machine interior (DB1 B1)
49 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].16 | 17 | 10.168.100.11 | LSK: Deviation Alarm - Water sump (DA1 B1)
50 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].17 | 18 | 10.168.100.11 | LSK: Deviation Alarm - Water table (DA1 B2)
51 | [M5090]Program:Enrober.Fault.M5AddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[1].18 | 19 | 10.168.100.11 | LSK: Deviation alarm - Machine interior(DB1 B1)
LSK 2 Tunnel
65 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].0 | 1 | 10.168.100.11 | LSK: Local isolator belt drive (CE1 M1)
66 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].1 | 2 | 10.168.100.11 | LSK: Air pressure belt tension (CE1 B5)
67 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].2 | 3 | 10.168.100.11 | LSK: Local isolator blower section 1 (El1 M1)
68 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].3 | 4 | 10.168.100.11 | LSK: Local isolator blower section 2 (EL1 M3)
69 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].4 | 5 | 10.168.100.11 | LSK: Iinfeed table not in top position (FC1 S1)
70 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].5 | 6 | 10.168.100.11 | LSK: Discharge table not in top position (FD1 S1)
71 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].6 | 7 | 10.168.100.11 | LSK: Spare LskAddFault bit 6
72 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].7 | 8 | 10.168.100.11 | LSK: Fuse block control voltage
73 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].8 | 9 | 10.168.100.11 | LSK: Estop cooler infeed left hand side (AE1 S1)
74 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].9 | 10 | 10.168.100.11 | LSK: Estop cooler infeed right hand side (AE1 S2)
75 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].10 | 11 | 10.168.100.11 | LSK: Estop cooler discharge left hand side (AE1 S3)
76 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].11 | 12 | 10.168.100.11 | LSK: Estop cooler discharge right hand side (AE1 S4)
77 | [M5090]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[5].12 | 13 | 10.168.100.11 | LSK: Estop cooler cabinet (AE1 S7)
78 | [M5090}Program:Tunnel.Fault.LskAddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[6].0 | 1 | 10.168.100.11 | LSK: Temperature Min Alarm - Air section 1 (EL1 B2)
79 | [M5090}Program:Tunnel.Fault.LskAddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[6].1 | 2 | 10.168.100.11 | LSK: Temperature Min Alarm - Air section 2 (EL1 B4)
86 | [M5090}Program:Tunnel.Fault.LskAddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[6].8 | 9 | 10.168.100.11 | LSK: Temperature Max Alarm - Air section 1 (EL1 B2)
87 | [M5090}Program:Tunnel.Fault.LskAddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[6].9 | 10 | 10.168.100.11 | LSK: Temperature Max Alarm - Air section 2 (EL1 B4)
94 | [M5090}Program:Tunnel.Fault.LskAddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[6].16 | 17 | 10.168.100.11 | LSK: Temperature deviation Air section 1 (EL1 B2)
95 | [M5090}Program:Tunnel.Fault.LskAddFault1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[6].17 | 18 | 10.168.100.11 | LSK: Temperature deviation Air section 2 (EL1 B4)
M5 090 Enrober
110 | [M5090}Program:Enrober .Fault .Tempering | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].0 | 1 | 10.168.100.11 | M5: Tempering
111 | [M5090}Program:Enrober .Fault .Enable | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].1 | 1 | 10.168.100.11 | M5: Enable
112 | [M5090}Program:Enrober .Fault .WaterPumpSump | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].2 | 1 | 10.168.100.11 | M5: Water pump sump (DA1 M1)
113 | [M5090}Program:Enrober .Fault .WaterPumpTable | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].3 | 1 | 10.168.100.11 | M5: Water pump table (DA2 M1)
114 | [M5090}Program:Enrober .Fault .Decorator | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].4 | 1 | 10.168.100.11 | M5: Decorator
115 | [M5090}Program:Enrober .Fault .NozzleCleaning | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].5 | 1 | 10.168.100.11 | M5: Nozzle cleaning
116 | [M5090}Program:Enrober .Fault .Screw | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].8 | 1 | 10.168.100.11 | M5: Screw drive (CC1 M1)
117 | [M5090}Program:Enrober .Fault .ScrewReverse | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].9 | 1 | 10.168.100.11 | M5: ScrewReverse
118 | [M5090}Program:Enrober .Fault .ReturnPumpAuto | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].10 | 1 | 10.168.100.11 | M5: Return pump (CH1 M1)
119 | [M5090}Program:Enrober .Fault .ReturnPumpMan | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].11 | 1 | 10.168.100.11 | M5: ReturnPumpMan
120 | [M5090}Program:Enrober .Fault .WireBelt | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].12 | 1 | 10.168.100.11 | M5: Wire belt (CE1 M1)
121 | [M5090}Program:Enrober .Fault .Detailer | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].13 | 1 | 10.168.100.11 | M5: Detailer (CX1 M1)
122 | [M5090}Program:Enrober .Fault .DetailerRev | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].14 | 1 | 10.168.100.11 | M5: DetailerRev
123 | [M5090}Program:Enrober .Fault .Blower1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].15 | 1 | 10.168.100.11 | M5: Blower 1 (CR1 M1)
124 | [M5090}Program:Enrober .Fault .Blower2 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].16 | 1 | 10.168.100.11 | M5: Blower 2 (CR2 M1)
125 | [M5090}Program:Enrober .Fault .LickingRoller | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].17 | 1 | 10.168.100.11 | M5: Licking rollerr (CU1 M1)
126 | [M5090}Program:Enrober .Fault .LickingRollerRev | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].18 | 1 | 10.168.100.11 | M5: Licking roller Reverse (CU1 M1)
127 | [M5090}Program:Enrober .Fault .Shaker | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].19 | 1 | 10.168.100.11 | M5: Shaker (CT1 M1)
128 | [M5090}Program:Enrober .Fault .BottomingRoller | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].20 | 1 | 10.168.100.11 | M5: Bottoming roller (CQ1 M1)
129 | [M5090}Program:Enrober .Fault .CurtainRoller | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].21 | 1 | 10.168.100.11 | M5: Curtain roller (CN1 M1)
130 | [M5090}Program:Enrober .Fault .InfeedTable | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].22 | 1 | 10.168.100.11 | M5: Infeed table
131 | [M5090}Program:Enrober .Fault .BlowOffDevice | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].23 | 1 | 10.168.100.11 | M5: Blow off device
132 | [M5090}Program:Enrober .Fault .MachineLights | ComData_M5_090_Alpha_To_Skynet.Fault_Data[3].27 | 1 | 10.168.100.11 | M5: Machine lights (DC1 M1)
LSK 2 Tunnel
133 | [M5090}Program:Tunnel .Fault .Lsk1BlowerSection1 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[8].8 | 1 | 10.168.100.11 | LSK: Blower section 1 (EL1 M1)
134 | [M5090}Program:Tunnel .Fault .Lsk1BlowerSection2 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[8].9 | 1 | 10.168.100.11 | LSK: Blower section 2 (EL1 M3)
135 | [M5090}Program:Tunnel .Fault .Lsk1WaterPumpSection1u2 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[8].10 | 1 | 10.168.100.11 | LSK: Water pump section 1+2
136 | [M5090}Program:Tunnel .Fault .Lsk1BlowerSection3 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[8].11 | 1 | 10.168.100.11 | LSK: Blower section 3
137 | [M5090}Program:Tunnel .Fault .Lsk1BlowerSection4 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[8].12 | 1 | 10.168.100.11 | LSK: Blower section 4
138 | [M5090}Program:Tunnel .Fault .Lsk1WaterPumpSection3u4 | ComData_M5_090_Alpha_To_Skynet.Fault_Data[8].13 | 1 | 10.168.100.11 | LSK: Water pump section 3+4
139 | [M5090}Program:Tunnel .Fault .Lsk1BeltDrive | ComData_M5_090_Alpha_To_Skynet.Fault_Data[8].16 | 1 | 10.168.100.11 | LSK: Belt drive (EE1 M1)
Controller Data:
Data# |  | Tag name | Value | Path IP | Description | Python Variable Name
Status Bits
1 | [M5090]AlarmPresent | [Skynet]ComData_M5_090_Alpha_To Skynet.Status_Bits[0].0 | 1 | 10.168.100.11 | Fault Present
2 | [M5090]Fb.Enable AND Fb.WireBelt AND Fb.Tempering | [Skynet]ComData_M5_090_Alpha_To Skynet.Status_Bits[0].1 | 1 | 10.168.100.11 | Production Active @ Line Speed
Parameters
3 | [M5090]RunningProgram | [Skynet]ComData_M5_090_Alpha_To Skynet.Parameters[0] | Var | 10.168.100.11 | Selected Recipe | m5_090_selected_recipie
Process Values
4 | [M5090]Enrober:ActData.Temp.Chocolate | [Skynet]ComData_M5_090_Alpha_To Skynet.Process_Values[8] | Var | 10.168.100.11 | Actual Temperature Chocolate | m5_090_actual_temp_chocolate
5 | [M5090]Enrober:ActData.Temp.WaterSump | [Skynet]ComData_M5_090_Alpha_To Skynet.Process_Values[9] | Var | 10.168.100.11 | Actual Temperature Water Sump | m5_090_actual_temp_water_sump
6 | [M5090]Enrober:ActData.Temp.WaterTable | [Skynet]ComData_M5_090_Alpha_To Skynet.Process_Values[10] | Var | 10.168.100.11 | Actual Temperature Water Table | m5_090_actual_temp_water_table
7 | [M5090]Enrober:ActData.Temp.MachineInterior | [Skynet]ComData_M5_090_Alpha_To Skynet.Process_Values[11] | Var | 10.168.100.11 | Actual Temperature Machine Interior | m5_090_actual_temp_machine_interior
8 | [M5090]Tunnel:ActData.Temp.Lsk1AirSection1 | [Skynet]ComData_M5_090_Alpha_To Skynet.Process_Values[0] | Var | 10.168.100.11 | Actual Temperature Cooling Tunnel 1 Section 1 | m5_090_actual_temperature_cooling_tunnel1_section1
9 | [M5090]Tunnel:ActData.Temp.Lsk1AirSection2 | [Skynet]ComData_M5_090_Alpha_To Skynet.Process_Values[1] | Var | 10.168.100.11 | Actual Temperature Cooling Tunnel 1 Section 2 | m5_090_actual_temperature_cooling_tunnel1_section2
Setpoint Values
10 | [M5090]Enrober:Setpoints.Speeds.Wirebelt | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[5] | Var | 10.168.100.11 | Setpoint Speed Wire Belt | m5_090_setpoints_speed_wire_belt
11 | [M5090]Enrober:Setpoints.Speeds.BottomingRoller | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[6] | Var | 10.168.100.11 | Setpoint Speed Bottom Roller | m5_090_setpoints_speed_bottom_roller
12 | [M5090]Enrober:Setpoints.Speeds.Shaker | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[7] | Var | 10.168.100.11 | Setpoint Speed Shaker | m5_090_setpoints_speed_shaker
13 | [M5090]Enrober:Setpoints.Speeds.Detailer | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[8] | Var | 10.168.100.11 | Setpoint Speed Detailer | m5_090_setpoints_speed_detailer
14 | [M5090]Enrober:Setpoints.Speeds.Blower1 | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[9] | Var | 10.168.100.11 | Setpoint Speed Blower 1 | m5_090_setpoints_speed_blower_1
15 | [M5090]Enrober:Setpoints.Speeds.Blower2 | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[10] | Var | 10.168.100.11 | Setpoint Speed Blower 2 | m5_090_setpoints_speed_blower_2
16 | [M5090]Enrober:Setpoints.Speeds.CurtainRoller | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[11] | Var | 10.168.100.11 | Setpoint Speed Curtain Roller | m5_090_setpoints_speed_curtain_roller
17 | [M5090]Enrober:Setpoints.Speeds.LickingRoller | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[12] | Var | 10.168.100.11 | Setpoint Speed Licking Roller | m5_090_setpoints_speed_licking_roller
18 | [M5090]Enrober:Setpoints.Temp. Chocolate | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[13] | Var | 10.168.100.11 | Setpoint Chocolate Temperature | m5_090_setpoint_chocolate_temp
19 | [M5090]Enrober:Setpoints.Temp.WaterSump | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[14] | Var | 10.168.100.11 | Setpoint Temperature Machine Interior | m5_090_setpoints_temp_machine_interior
20 | [M5090]Enrober:Setpoints.Temp.WaterTable | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[15] | Var | 10.168.100.11 | Setpoint Temperature Water Table | m5_090_setpoints_temp_water_table
21 | [M5090]Enrober:Setpoints.Temp. MachineInterior | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[16] | Var | 10.168.100.11 | Setpoint Temperature Water Sump | m5_090_setpoints_temp_water_sump
22 | [M5090]Tunnel:Setpoints.Temp.LskAirSection1 | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[20] | Var | 10.168.100.11 | Setpoint Temperature Cooling Tunnel 1 Section 1 | m5_090_setpoint_temperature_cooling_tunnel1_section1
23 | [M5090]Tunnel:Setpoints.Temp.LskAirSection2 | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[21] | Var | 10.168.100.11 | Setpoint Temperature Cooling Tunnel 1 Section 2 | m5_090_setpoint_temperature_cooling_tunnel1_section2
24 | [M5090]Tunnel:Setpoints.Speeds.Lsk1BeltDrive | [Skynet]ComData_M5_090_Alpha_To Skynet.Setpoint_Values[22] | Var | 10.168.100.11 | Setpoint Speed Lsk Belt Drive (Tunnel 2) | m5_090_setpoint_speed_lsk_belt_drive_tunnel2

## Alpha TT 100
HMI Fault Messages:
TT 100 Tempering
140 | [TT100]Program:Temper.Fault.Tempering | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].0 | 1 | 10.168.100.11 | Temperieren
141 | [TT100]Program:Temper.Fault.Enable | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].1 | 1 | 10.168.100.11 | Enable
142 | [TT100]Program:Temper.Fault.WaterPumpHST | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].2 | 1 | 10.168.100.11 | Water pump heating stage
143 | [TT100]Program:Temper.Fault.WaterPumpCST | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].3 | 1 | 10.168.100.11 | Water pump cooling stage
144 | [TT100]Program:Temper.Fault.WaterPumpMST | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].4 | 1 | 10.168.100.11 | Water pump mixing stage
145 | [TT100]Program:Temper.Fault.WaterPumpPipe | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].5 | 1 | 10.168.100.11 | Water pump chocolate pipe
146 | [TT100]Program:Temper.Fault.Scraper | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].6 | 1 | 10.168.100.11 | Scraper drive
147 | [TT100]Program:Temper.Fault.FeedPump | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].7 | 1 | 10.168.100.11 | Feedpump
148 | [TT100]Program:Temper.Fault.FeedPumpRev | ComData_TT_100_Alpha_To_Skynet.Fault_Data[3].8 | 1 | 10.168.100.11 | Feed pump reverse
149 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].0 | 1 | 10.168.100.11 | Temperature low
150 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].1 | 2 | 10.168.100.11 | High chocolate pressure
151 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].2 | 3 | 10.168.100.11 | Enrober Not Ready
152 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].3 | 4 | 10.168.100.11 | Thermistor scraper
153 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].4 | 5 | 10.168.100.11 | Local isolator feed pump
154 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].5 | 6 | 10.168.100.11 | Chocolate pipe not clear
155 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].6 | 7 | 10.168.100.11 | Scraper drive switch off due to feed pump stop
156 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].7 | 8 | 10.168.100.11 | Fuse block control voltage 24VDC
157 | [TT100]Program:Temper.Fault.TCAddFault0 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[0].31 | 32 | 10.168.100.11 | Ethernet communication to M5
158 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].0 | 1 | 10.168.100.11 | Temperature min alarm heating stage
159 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].1 | 2 | 10.168.100.11 | Temperature min alarm water cooling stage
160 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].2 | 3 | 10.168.100.11 | Temperature min alarm chocolate cooling stage
161 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].3 | 4 | 10.168.100.11 | Temperature min alarm water mixing stage
162 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].4 | 5 | 10.168.100.11 | Temperature min alarm water pipe
163 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].5 | 6 | 10.168.100.11 | Drive16
164 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].8 | 9 | 10.168.100.11 | Temperature max alarm heating stage
165 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].9 | 10 | 10.168.100.11 | Temperature max alarm water cooling stage
166 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].10 | 11 | 10.168.100.11 | Temperature max alarm chocolate cooling stage
167 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].11 | 12 | 10.168.100.11 | Temperature max alarm water mixing stage
168 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].12 | 13 | 10.168.100.11 | Temperature max alarm water pipe
169 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].13 | 14 | 10.168.100.11 | Drive22
170 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].16 | 17 | 10.168.100.11 | Temperature deviation heating stage
171 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].17 | 18 | 10.168.100.11 | Temperature deviation water cooling stage
172 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].18 | 19 | 10.168.100.11 | Temperature deviation chocolate cooling stage
173 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].19 | 20 | 10.168.100.11 | Temperature min alarm water mixing stage
174 | [TT100]Program:Temper.Fault.TCAddFault1 | ComData_TT_100_Alpha_To_Skynet.Fault_Data[1].20 | 21 | 10.168.100.11 | Temperature min alarm water pipe
Controller Data:
Data# |  | Tag name | Value | Path IP | Description | Python Variable Name
Status Bits
1 | [TTB015]Tempering:AlarmPresent | [Skynet]ComData_TT_100_Alpha_To_Skynet.Status_Bits[0].0 | 1 | 10.168.100.10 | Fault Present
2 | [TTB015]Tempering:Fb.Tempering | [Skynet]ComData_TT_100_Alpha_To_Skynet.Status_Bits[0].1 | 1 | 10.168.100.10 | Running
Parameters
3 | [TTB015]Tempering:RunningProgram | [Skynet]ComData_TT_100_Alpha_To_Skynet.Parameters[0] | Var | 10.168.100.10 | Selected Program | tt_100_selected_program
Process Values
1 | [TT100]Tempering:ActData.Temp.ChocolateInfeed | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[0] | Var | 10.168.100.10 | Actual Temperature Chocolate Infeed | tt_100_actual_temp_chocolate_infeed
2 | [TT100]Tempering:ActData.Temp.HeatingStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[1] | Var | 10.168.100.10 | Actual Temperature Heating Stage | tt_100_actual_temp_heating_stage
3 | [TT100]Tempering:ActData.Temp.WaterHeatStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[2] | Var | 10.168.100.10 | Actual Temperature Water Heat Stage | tt_100_actual_temp_water_heat_stage
4 | [TT100]Tempering:ActData.Temp.ChocHeatStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[3] | Var | 10.168.100.10 | Actual Temperature Chocolate Heat Stage | tt_100_actual_temp_chocolate_heat_stage
5 | [TT100]Tempering:ActData.Temp.WaterCoolStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[4] | Var | 10.168.100.10 | Actual Temperature Water Cool Stage | tt_100_actual_temp_water_cool_stage_
6 | [TT100]Tempering:ActData.Temp.ChocCoolStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[5] | Var | 10.168.100.10 | Actual Temperature Chocolate Cool Stage | tt_100_actual_temp_choc_cool_stage
7 | [TT100]Tempering:ActData.Temp.WaterMixStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[6] | Var | 10.168.100.10 | Actual Temperature Water Mix Stage | tt_100_actual_temp_water_mix_stage
8 | [TT100]Tempering:ActData.Temp.ChocMixstage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[7] | Var | 10.168.100.10 | Actual Temperature Chocolate Mix Stage | tt_100_actual_temp_choc_mix_stage
9 | [TT100]Tempering:ActData.Temp.WaterChocPipe | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[8] | Var | 10.168.100.10 | Actual Temperature Water Chocolate Pipe | tt_100_actual_temp_water_choc_pipe
10 | [TT100]Tempering:ActData.Data.ChocPressure | [Skynet]ComData_TT_100_Alpha_To_Skynet.Process_Values[9] | Var | 10.168.100.10 | Actual Pump Discharge Pressure | tt_100_actual_pump_discharge_pressure
Setpoint Values
11 | [TT100]Tempering:Setpoints.Temp.ChocolateInfeed | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[0] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Infeed | tt_100_setpoint_temp_chocolate_infeed
12 | [TT100]Tempering:Setpoints.Temp.HeatingStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[1] | Var | 10.168.100.10 | Setpoint Temperature Heating Stage | tt_100_setpoint_temp_heating_stage
31 | [TT100]Tempering:Setpoints.Temp.WaterHeatStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[2] | Var | 10.168.100.10 | Setpoint Temperature Water Heat Stage | tt_100_setpoint_temp_water_heat_stage
32 | [TT100]Tempering:Setpoints.Temp.ChocHeatStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[3] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Heat Stage | tt_100_setpoint_temp_chocolate_heat_stage
33 | [TT100]Tempering:Setpoints.Temp.WaterCoolStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[4] | Var | 10.168.100.10 | Setpoint Temperature Water Cool Stage | tt_100_setpoint_temp_water_cool_stage_
34 | [TT100]Tempering:Setpoints.Temp.ChocCoolStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[5] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Cool Stage | tt_100_setpoint_temp_choc_cool_stage
35 | [TT100]Tempering:Setpoints.Temp.WaterMixStage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[6] | Var | 10.168.100.10 | Setpoint Temperature Water Mix Stage | tt_100_setpoint_temp_water_mix_stage
36 | [TT100]Tempering:Setpoints.Temp.ChocMixstage | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[7] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Mix Stage | tt_100_setpoint_temp_choc_mix_stage
37 | [TT100]Tempering:Setpoints.Temp.WaterChocPipe | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[8] | Var | 10.168.100.10 | Setpoint Temperature Water Chocolate Pipe | tt_100_setpoint_temp_water_choc_pipe
38 | [TT100]Tempering:Setpoints.Speeds.FeedPump | [Skynet]ComData_TT_100_Alpha_To_Skynet.Setpoint_Values[9] | Var | 10.168.100.10 | Setpoint Feed Pump (kg/hr) | tt_100_setpoint_feed_pump_kg_hr

## Alpha M5 140
HMI Fault Messages:
Alarm # | Processor OEM Tag | Data Concentrator Tag | Value | Path IP | Message
M5 140 Enrober
1 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].0 | 1 | 10.168.100.12 | M5: Low start temperature
2 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].1 | 1 | 10.168.100.12 | M5: Service cover sump open
4 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].3 | 1 | 10.168.100.12 | M5: Air pressure wire belt
5 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].4 | 1 | 10.168.100.12 | M5: Wire belt tension operator side fully extended (CE1 B7)
6 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].5 | 1 | 10.168.100.12 | M5: Wire belt tension operator side fully contracted (CE1 B6)
7 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].6 | 1 | 10.168.100.12 | M5: Wire belt tension drive side fully extended (CE1 B4)
8 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].7 | 1 | 10.168.100.12 | M5: Wire belt tension drive side fully contracted (CE1 B3)
9 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].8 | 1 | 10.168.100.12 | M5: Chocolate valve in front of return pump closed (CH1 S2)
10 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].9 | 1 | 10.168.100.12 | M5: Chocolate valve behind return pump closed (CH1 S3)
11 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].10 | 1 | 10.168.100.12 | M5: Chocolate return path not clear
12 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].11 | 1 | 10.168.100.12 | M5: Local isolator return pump (CH1 M1)
13 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].12 | 1 | 10.168.100.12 | M5: Curtain roller not plugged in
14 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].13 | 1 | 10.168.100.12 | M5: Fuse block 24VDC
15 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].14 | 1 | 10.168.100.12 | M5: Detailer not plugged in (CX1 M1)
17 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].16 | 1 | 10.168.100.12 | M5: Emergency stop left hand side (AE1 S3)
18 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].17 | 1 | 10.168.100.12 | M5: Emergency stop right hand side (AE1 S4)
22 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].21 | 1 | 10.168.100.12 | M5_140: Emergency stop in that area
23 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].22 | 1 | 10.168.100.12 | M5 1: Emergency stop in that area
24 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].23 | 1 | 10.168.100.12 | Please press reset i.o. to reset Estop relay
28 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].27 | 1 | 10.168.100.12 | M5: PointIO communication to decorator cabinet failed
29 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].28 | 1 | 10.168.100.12 | M5: PointIO communication to final cooler cabinet failed
30 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].29 | 1 | 10.168.100.12 | M5: Ethernet communication to M5_140
31 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].30 | 1 | 10.168.100.12 | M5: Ethernet communication to M5 1
32 | [M5140]Program:Enrober.Fault.M5AddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[0].31 | 1 | 10.168.100.12 | M5: Ethernet communication to TT
33 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].0 | 1 | 10.168.100.12 | LSK: Min Alarm - Water sump (DA1 B1)
34 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].1 | 1 | 10.168.100.12 | LSK: Min Alarm - Water table (DA1 B2)
35 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].2 | 1 | 10.168.100.12 | LSK: Min alarm - Machine interior (DB1 B1)
41 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].8 | 1 | 10.168.100.12 | LSK: Max Alarm - Water sump (DA1 B1)
42 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].9 | 1 | 10.168.100.12 | LSK: Max Alarm - Water table (DA1 B2)
43 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].10 | 1 | 10.168.100.12 | LSK: Max Alarm - Machine interior (DB1 B1)
49 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].16 | 1 | 10.168.100.12 | LSK: Deviation Alarm - Water sump (DA1 B1)
50 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].17 | 1 | 10.168.100.12 | LSK: Deviation Alarm - Water table (DA1 B2)
51 | [M5140]Program:Enrober.Fault.M5AddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[1].18 | 1 | 10.168.100.12 | LSK: Deviation alarm - Machine interior (DB1 B1)
LSK 3 Tunnel
52 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].0 | 1 | 10.168.100.12 | LSK: Local isolator belt drive (CE1 M1)
53 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].1 | 1 | 10.168.100.12 | LSK: Air pressure belt tension (CE1 B5)
54 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].2 | 1 | 10.168.100.12 | LSK: Local isolator blower section 1 (El1 M1)
55 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].3 | 1 | 10.168.100.12 | LSK: Local isolator blower section 2 (EL1 M3)
56 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].4 | 1 | 10.168.100.12 | LSK: Iinfeed table not in top position (FC1 S1)
57 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].5 | 1 | 10.168.100.12 | LSK: Discharge table not in top position (FD1 S1)
58 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].6 | 1 | 10.168.100.12 | LSK: Spare LskAddFault bit 6
59 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].7 | 1 | 10.168.100.12 | LSK: Fuse block control voltage
60 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].8 | 1 | 10.168.100.12 | LSK: Estop final cooler infeed left hand side (AE1 S1)
61 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].9 | 1 | 10.168.100.12 | LSK: Estop final cooler infeed right hand side (AE1 S2)
62 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].10 | 1 | 10.168.100.12 | LSK: Estop final cooler discharge left hand side (AE1 S3)
63 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].11 | 1 | 10.168.100.12 | LSK: Estop final cooler discharge right hand side (AE1 S4)
64 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].12 | 1 | 10.168.100.12 | LSK: Estop final cooler cabinet (AE1 S7)
65 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].13 | 1 | 10.168.100.12 | CT: Emergency stop cooling table / Dc4 cabinet (AE1 S7)
66 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].14 | 1 | 10.168.100.12 | CT: Emergency stop cooling table infeed left (AE1 S1)
67 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].15 | 1 | 10.168.100.12 | CT: Emergency stop cooling table infeed right (AE1 S2)
68 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].16 | 1 | 10.168.100.12 | CT: Emergency stop cooling table discharge left (AE1 S3)
69 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].17 | 1 | 10.168.100.12 | CT: Emergency stop cooling table discharge right (AE1 S4)
70 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].20 | 1 | 10.168.100.12 | LSK: Schieberegister DC4 zu kurz
71 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].24 | 1 | 10.168.100.12 | CT: Local isolator water pump bottoming cooling (HA1 M1)
72 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].25 | 1 | 10.168.100.12 | CT: Local isolator belt drive (EE1 M1)
73 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].26 | 1 | 10.168.100.12 | CT: Air pressure belt tension (FD1 M1)
74 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].27 | 1 | 10.168.100.12 | CT: Local isolator discharge screw (CW1 M1)
75 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].28 | 1 | 10.168.100.12 | CT: Local isolator collect tank return pump (CH1 M1)
76 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].29 | 1 | 10.168.100.12 | CT: Cooling table infeed not in top position (FC1 S1)
77 | [M5140]Program:Tunnel.Fault.LskAddFault0 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[5].30 | 1 | 10.168.100.12 | CT: Collect tank not in position (AM1 S3)
78 | [M5140]Program:Tunnel.Fault.LskAddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[6].0 | 1 | 10.168.100.12 | LSK: Temperature Min Alarm - Air section 1 (EL1 B2)
79 | [M5140]Program:Tunnel.Fault.LskAddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[6].1 | 1 | 10.168.100.12 | LSK: Temperature Min Alarm - Air section 2 (EL1 B4)
80 | [M5140]Program:Tunnel.Fault.LskAddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[6].8 | 1 | 10.168.100.12 | LSK: Temperature Max Alarm - Air section 1 (EL1 B1)
81 | [M5140]Program:Tunnel.Fault.LskAddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[6].9 | 1 | 10.168.100.12 | LSK: Temperature Max Alarm - Air section 2 (EL1 B2)
82 | [M5140]Program:Tunnel.Fault.LskAddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[6].16 | 1 | 10.168.100.12 | LSK: Temperature deviation Air section 1 (EL1 B1)
83 | [M5140]Program:Tunnel.Fault.LskAddFault1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[6].17 | 1 | 10.168.100.12 | LSK: Temperature deviation Air section 2 (EL1 B2)
M5 140 Enrober
84 | [M5140]Program:Enrober.Fault.Tempering | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].0 | 1 | 10.168.100.12 | M5: Tempering
85 | [M5140]Program:Enrober.Fault.Enable | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].1 | 1 | 10.168.100.12 | M5: Enable
86 | [M5140]Program:Enrober.Fault.WaterPumpSump | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].2 | 1 | 10.168.100.12 | M5: Water pump sump (DA1 M1)
87 | [M5140]Program:Enrober.Fault.WaterPumpTable | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].3 | 1 | 10.168.100.12 | M5: Water pump table (DA2 M1)
88 | [M5140]Program:Enrober.Fault.Decorator | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].4 | 1 | 10.168.100.12 | M5: Decorator
89 | [M5140]Program:Enrober.Fault.NozzleCleaning | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].5 | 1 | 10.168.100.12 | M5: Nozzle cleaning
90 | [M5140]Program:Enrober.Fault.Screw | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].8 | 1 | 10.168.100.12 | M5: Screw drive (CC1 M1)
91 | [M5140]Program:Enrober.Fault.ScrewReverse | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].9 | 1 | 10.168.100.12 | M5: ScrewReverse
92 | [M5140]Program:Enrober.Fault.ReturnPumpAuto | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].10 | 1 | 10.168.100.12 | M5: Return pump (CH1 M1)
93 | [M5140]Program:Enrober.Fault.ReturnPumpMan | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].11 | 1 | 10.168.100.12 | M5: ReturnPumpMan
94 | [M5140]Program:Enrober.Fault.WireBelt | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].12 | 1 | 10.168.100.12 | M5: Wire belt (CE1 M1)
95 | [M5140]Program:Enrober.Fault.Detailer | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].13 | 1 | 10.168.100.12 | M5: Detailer (CX1 M1)
96 | [M5140]Program:Enrober.Fault.DetailerRev | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].14 | 1 | 10.168.100.12 | M5: DetailerRev
97 | [M5140]Program:Enrober.Fault.Blower1 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].15 | 1 | 10.168.100.12 | M5: Blower 1 (CR1 M1)
98 | [M5140]Program:Enrober.Fault.Blower2 | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].16 | 1 | 10.168.100.12 | M5: Blower 2 (CR2 M1)
99 | [M5140]Program:Enrober.Fault.LickingRoller | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].17 | 1 | 10.168.100.12 | M5: Licking roller (CU1 M1)
100 | [M5140]Program:Enrober.Fault.LickingRollerRev | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].18 | 1 | 10.168.100.12 | M5: Licking roller Reverse (CU1 M1)
101 | [M5140]Program:Enrober.Fault.Shaker | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].19 | 1 | 10.168.100.12 | M5: Shaker (CT1 M1)
102 | [M5140]Program:Enrober.Fault.BottomingRoller | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].20 | 1 | 10.168.100.12 | M5: Bottoming roller (CQ1 M1)
103 | [M5140]Program:Enrober.Fault.CurtainRoller | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].21 | 1 | 10.168.100.12 | M5: Curtain roller (CN1 M1)
104 | [M5140]Program:Enrober.Fault.InfeedTable | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].22 | 1 | 10.168.100.12 | M5: Infeed table
105 | [M5140]Program:Enrober.Fault.BlowOffDevice | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].23 | 1 | 10.168.100.12 | M5: Blow off device
106 | [M5140]Program:Enrober.Fault.MachineLights | ComData_M5_140_Alpha_To_Skynet.Fault_Data[3].27 | 1 | 10.168.100.12 | M5: Machine lights (DC1 M1)
LSK 3 Tunnel
107 | [M5140]Program:Tunnel.Fault.Lsk1BlowerSection1 | ComData_M5_140_Alpha_To_Skynet[8].8 | 1 | 10.168.100.12 | LSK: Blower section 1 (EL1 M1)
108 | [M5140]Program:Tunnel.Fault.Lsk1BlowerSection2 | ComData_M5_140_Alpha_To_Skynet[8].9 | 1 | 10.168.100.12 | LSK: Blower section 2 (EL1 M3)
109 | [M5140]Program:Tunnel.Fault.Lsk1WaterPumpSection1u2 | ComData_M5_140_Alpha_To_Skynet[8].10 | 1 | 10.168.100.12 | LSK: Water pump section 1+2
110 | [M5140]Program:Tunnel.Fault.Lsk1BlowerSection3 | ComData_M5_140_Alpha_To_Skynet[8].11 | 1 | 10.168.100.12 | LSK: Blower section 3
111 | [M5140]Program:Tunnel.Fault.Lsk1BlowerSection4 | ComData_M5_140_Alpha_To_Skynet[8].12 | 1 | 10.168.100.12 | LSK: Blower section 4
112 | [M5140]Program:Tunnel.Fault.Lsk1WaterPumpSection3u4 | ComData_M5_140_Alpha_To_Skynet[8].13 | 1 | 10.168.100.12 | LSK: Water pump section 3+4
113 | [M5140]Program:Tunnel.Fault.Lsk1BeltDrive | ComData_M5_140_Alpha_To_Skynet[8].16 | 1 | 10.168.100.12 | LSK: Belt drive (EE1 M1)
114 | [M5140]Program:Tunnel.Fault.DC4 | ComData_M5_140_Alpha_To_Skynet[8].24 | 1 | 10.168.100.12 | LSK: DC4 (AK1 M1)
115 | [M5140]Program:Tunnel.Fault.Dc4Slave | ComData_M5_140_Alpha_To_Skynet[8].26 | 1 | 10.168.100.12 | LSK: DC4 slave (AK1 M2)
116 | [M5140]Program:Tunnel.Fault.DC4NozzleCleaning | ComData_M5_140_Alpha_To_Skynet[8].25 | 1 | 10.168.100.12 | LSK: Nozzle cleaning
117 | [M5140]Program:Tunnel.Fault.CollectTankScrew | ComData_M5_140_Alpha_To_Skynet[8].17 | 1 | 10.168.100.12 | LSK: Collect tank discharge screw (CW1 M1)
118 | [M5140]Program:Tunnel.Fault.CollectTankReturnPump | ComData_M5_140_Alpha_To_Skynet[8].18 | 1 | 10.168.100.12 | LSK: Collect tank return pump (CH1 M1)
119 | [M5140]Program:Tunnel.Fault.CtBeltDrive | ComData_M5_140_Alpha_To_Skynet[8].21 | 1 | 10.168.100.12 | CT: Belt drive (EE1 M1)
120 | [M5140]Program:Tunnel.Fault.CtWaterPump | ComData_M5_140_Alpha_To_Skynet[8].22 | 1 | 10.168.100.12 | CT: Water pump bottoming cooling (HA1 M1)
Controller Data:
Data# |  | Tag name | Value | Path IP | Description | Python Variable Name
Status Bits
1 | [M5140]AlarmPresent | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Status_Bits[0].0 | 1 | 10.168.100.12 | Fault Present
2 | [M5140]Fb.Enable AND Fb.WireBelt AND Fb.Tempering | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Status_Bits[0].1 | 1 | 10.168.100.12 | Production Active
Parameters
3 | [M5140]RunningProgram | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Parameters[0] | 0 | 10.168.100.12 | Selected Recipe | m5_140_selected_recipie
Process Values
4 | [M5140]Enrober:ActData.Temp.Chocolate | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[8] | Var | 10.168.100.12 | Actual Temperature Chocolate | m5_140_actual_temp_chocolate
5 | [M5140]Enrober:ActData.Temp.WaterSump | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[9] | Var | 10.168.100.12 | Actual Temperature Water Sump | m5_140_actual_temp_water_sump
6 | [M5140]Enrober:ActData.Temp.WaterTable | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[10] | Var | 10.168.100.12 | Actual Temperature Water Table | m5_140_actual_temp_water_table
7 | [M5140]Enrober:ActData.Temp.MachineInterior | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[11] | Var | 10.168.100.12 | Actual Temperature Machine Interior | m5_140_actual_temp_machine_interior
8 | [M5140]Tunnel:ActData.Temp.CtWaterBottomCooling | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[20] | Var | 10.168.100.12 | Actual Temperature Cooling Table Water | m5_140_actual_temp_cooling_wable_water
9 | [M5140]Tunnel:ActData.Temp.Lsk1AirSection1 | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[21] | Var | 10.168.100.12 | Actual Temperature Cooling Tunnel 1 Section 1 | m5_140_actual_temperature_cooling_tunnel1_section1
10 | [M5140]Tunnel:ActData.Temp.Lsk1AirSection2 | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[22] | Var | 10.168.100.12 | Actual Temperature Cooling Tunnel 1 Section 2 | m5_140_actual_temperature_cooling_tunnel1_section2
11 | [M5140]Tunnel:ActData.Temp.Dc4Interior | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Process_Values[23] | Var | 10.168.100.12 | Actual Temperature Decorator Interior | m5_140_actual_temp_decorator_interior
Setpoint Values
12 | [M5140]Enrober:Setpoints.Temp.WaterSump | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[1] | Var | 10.168.100.12 | Setpoint Temperature Water Sump | m5_140_setpoints_temp_water_sump
13 | [M5140]Enrober:Setpoints.Temp.WaterTable | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[2] | Var | 10.168.100.12 | Setpoint Temperature Water Table | m5_140_setpoints_temp_water_table
14 | [M5140]Enrober:Setpoints.Temp. MachineInterior | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[3] | Var | 10.168.100.12 | Setpoint Temperature Machine Interior | m5_140_setpoints_temp_machine_interior
15 | [M5140]Enrober:Setpoints.Speeds.Wirebelt | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[4] | Var | 10.168.100.12 | Setpoint Speed Wire Belt | m5_140_setpoints_speed_wire_belt
16 | [M5140]Enrober:Setpoints.Speeds.BottomingRoller | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[5] | Var | 10.168.100.12 | Setpoint Speed Bottom Roller | m5_140_setpoints_speed_bottom_roller
17 | [M5140]Enrober:Setpoints.Speeds.Shaker | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[6] | Var | 10.168.100.12 | Setpoint Speed Shaker | m5_140_setpoints_speed_shaker
18 | [M5140]Enrober:Setpoints.Speeds.Detailer | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[7] | Var | 10.168.100.12 | Setpoint Speed Detailer | m5_140_setpoints_speed_detailer
19 | [M5140]Enrober:Setpoints.Speeds.Blower1 | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[8] | Var | 10.168.100.12 | Setpoint Speed Blower 1 | m5_140_setpoints_speed_blower_1
20 | [M5140]Enrober:Setpoints.Speeds.Blower2 | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[9] | Var | 10.168.100.12 | Setpoint Speed Blower 2 | m5_140_setpoints_speed_blower_2
21 | [M5140]Enrober:Setpoints.Speeds.CurtainRoller | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[10] | Var | 10.168.100.12 | Setpoint Speed Curtain Roller | m5_140_setpoints_speed_curtain_roller
22 | [M5140]Enrober:Setpoints.Speeds.LickingRoller | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[11] | Var | 10.168.100.12 | Setpoint Speed Licking Roller | m5_140_setpoints_speed_licking_roller
23 | [M5140]Tunnel:Setpoints.Temp.CtWaterBottomCooling | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[20] | Var | 10.168.100.12 | Setpoint Temperature Cooling Table Water Bottom Cooling | m5_140_setpoints_temp_ct_water_bottom_cooling
24 | [M5140]Tunnel:Setpoints.Temp.Lsk1.AirSection1 | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[21] | Var | 10.168.100.12 | Setpoint Temperature Lsk1 Air Section 1 | m5_140_setpoints_temp_lsk1_air_section_1
25 | [M5140]Tunnel:Setpoints.Temp.Lsk1.AirSection2 | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[22] | Var | 10.168.100.12 | Setpoint Temperature Lsk1 Air Section 2 | m5_140_setpoints_temp_lsk1_air_section_2
26 | [M5140]Tunnel:Setpoints.Temp.Dc4Interior | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[23] | Var | 10.168.100.12 | Setpoint Temperature Decorator Interior | m5_140_setpoints_temp_decorator_interior
27 | [M5140]Tunnel:Setpoints.SpeedsCtBeltDrive | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[24] | Var | 10.168.100.12 | Setpoint Belt Speed Cooling Table | m5_140_setpoints_belt_speed_cooling_table
28 | [M5140]Tunnel:Setpoints.Speeds.Lsk1BeltDrive | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[25] | Var | 10.168.100.12 | Setpoint Speed Lsk Belt Drive Tunnel 2 | m5_140_setpoint_speed_lsk_belt_drive_tunnel2
29 | [M5140]Tunnel:Setpoints.Dc4.Velocity | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[30] | Var | 10.168.100.12 | Decorator Velocity | m5_140_decorator_velocity
30 | [M5140]Tunnel:Setpoints.Dc4.NoAxisToRun | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[31] | Var | 10.168.100.12 | Decorator Number of Axis | m5_140_decorator_number_of_axis
31 | [M5140]Tunnel:Setpoints.Dc4.SlavePhase | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[32] | Var | 10.168.100.12 | Decorator Timing | m5_140_decorator_timing
32 | [M5140]Tunnel:Setpoints.Dc4.AxisGearRatio | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[33] | Var | 10.168.100.12 | Decorator Ratio | m5_140_decorator_ratio
33 | [M5140]Tunnel:Setpoints.Dc4.Heater | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[34] | Var | 10.168.100.12 | Decorator Heater Output | m5_140_decorator_heater_output
34 | [M5140]Tunnel:Setpoints.Dc4.TimeSet_CleanInterval_InSec10th | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[35] | Var | 10.168.100.12 | Decorator Clean Interval | m5_140_decorator_clean_interval
35 | [M5140]Tunnel:Setpoints.Dc4.TimeSet_CleanPulseLength_InSec10th | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[36] | Var | 10.168.100.12 | Decorator Clean Pulse Time | m5_140_decorator_clean_pulse_time
36 | [M5140]Tunnel:Setpoints.Dc4.TimeSet_GapTime_InSec10th | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[37] | Var | 10.168.100.12 | Decorator Parameter | m5_140_decorator_parameter
37 | [M5140]Tunnel:Setpoints.Dc4.TimeSet_GapIntervalTime_InSec10th | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[38] | Var | 10.168.100.12 | Decorator Distance to Photo Eye | m5_140_decorator_distance_to_photoeye
38 | [M5140]Tunnel:Setpoints.Dc4.DistanceFotocellToNozzles | [Skynet]ComData_M5_140_Alpha_To_ Skynet.Setpoint_Values[39] | Var | 10.168.100.12 | Decorator Parameter

## Alpha TT 150
HMI Fault Messages:
Alarm | Tag name | Path IP | Value | Path IP | Message
Reporting Through M5 140
TT 100 Tempering
149 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].0 | 1 | 10.168.100.11 | Temperature low
150 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].1 | 1 | 10.168.100.11 | High chocolate pressure
151 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].2 | 1 | 10.168.100.11 | Enrober Not Ready
152 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].3 | 1 | 10.168.100.11 | Thermistor scraper
153 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].4 | 1 | 10.168.100.11 | Local isolator feed pump
154 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].5 | 1 | 10.168.100.11 | Chocolate pipe not clear
155 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].6 | 1 | 10.168.100.11 | Scraper drive switch off due to feed pump stop
156 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].7 | 1 | 10.168.100.11 | Fuse block control voltage 24VDC
157 | [TT150]Program:Temper.Fault.TCAddFault0 | ComData_TT_150_Alpha_To_Skynet[0].31 | 1 | 10.168.100.11 | Ethernet communication to M5
158 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].0 | 1 | 10.168.100.11 | Temperature min alarm heating stage
159 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].1 | 1 | 10.168.100.11 | Temperature min alarm water cooling stage
160 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].2 | 1 | 10.168.100.11 | Temperature min alarm chocolate cooling stage
161 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].3 | 1 | 10.168.100.11 | Temperature min alarm water mixing stage
162 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].4 | 1 | 10.168.100.11 | Temperature min alarm water pipe
164 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].8 | 1 | 10.168.100.11 | Temperature max alarm heating stage
165 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].9 | 1 | 10.168.100.11 | Temperature max alarm water cooling stage
166 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].10 | 1 | 10.168.100.11 | Temperature max alarm chocolate cooling stage
167 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].11 | 1 | 10.168.100.11 | Temperature max alarm water mixing stage
168 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].12 | 1 | 10.168.100.11 | Temperature max alarm water pipe
170 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].16 | 1 | 10.168.100.11 | Temperature deviation heating stage
171 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].17 | 1 | 10.168.100.11 | Temperature deviation water cooling stage
172 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].18 | 1 | 10.168.100.11 | Temperature deviation chocolate cooling stage
173 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].19 | 1 | 10.168.100.11 | Temperature min alarm water mixing stage
174 | [TT150]Program:Temper.Fault.TCAddFault1 | ComData_TT_150_Alpha_To_Skynet[1].20 | 1 | 10.168.100.11 | Temperature min alarm water pipe
140 | [TT150]Program:Temper.Fault.Tempering | ComData_TT_150_Alpha_To_Skynet[3].0 | 1 | 10.168.100.11 | Temperieren
141 | [TT150]Program:Temper.Fault.Enable | ComData_TT_150_Alpha_To_Skynet[3].1 | 1 | 10.168.100.11 | Enable
142 | [TT150]Program:Temper.Fault.WaterPumpHST | ComData_TT_150_Alpha_To_Skynet[3].2 | 1 | 10.168.100.11 | Water pump heating stage
143 | [TT150]Program:Temper.Fault.WaterPumpCST | ComData_TT_150_Alpha_To_Skynet[3].3 | 1 | 10.168.100.11 | Water pump cooling stage
144 | [TT150]Program:Temper.Fault.WaterPumpMST | ComData_TT_150_Alpha_To_Skynet[3].4 | 1 | 10.168.100.11 | Water pump mixing stage
145 | [TT150]Program:Temper.Fault.WaterPumpPipe | ComData_TT_150_Alpha_To_Skynet[3].5 | 1 | 10.168.100.11 | Water pump chocolate pipe
146 | [TT150]Program:Temper.Fault.Scraper | ComData_TT_150_Alpha_To_Skynet[3].6 | 1 | 10.168.100.11 | Scraper drive
147 | [TT150]Program:Temper.Fault.FeedPump | ComData_TT_150_Alpha_To_Skynet[3].7 | 1 | 10.168.100.11 | Feedpump
148 | [TT150]Program:Temper.Fault.FeedPumpRev | ComData_TT_150_Alpha_To_Skynet[3].8 | 1 | 10.168.100.11 | Feed pump reverse
Controller Data:
Data# | Tag name | Path IP | Value | Path IP | Description | Python Variable Name
Status Bits
1 | [TTB015]Tempering:AlarmPresent | [Skynet]ComData_TT_150_Alpha_to_Skynet.Status_Bits[0].0 | 1 | 10.168.100.10 | Fault Present
2 | [TTB015]Tempering:Fb.Tempering | [Skynet]ComData_TT_150_Alpha_to_Skynet.Status_Bits[0].1 | 1 | 10.168.100.10 | Running
Parameters
3 | [TTB015]Tempering:RunningProgram | [Skynet]ComData_TT_150_Alpha_to_Skynet.Parameters[0] | Var | 10.168.100.10 | Selected Program | tt_150_selected_program
Process Values
4 | [TT100]Tempering:ActData.Temp.ChocolateInfeed | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[0] | Var | 10.168.100.10 | Actual Temperature Chocolate Infeed | tt_150_actual_temp_chocolate_infeed
5 | [TT100]Tempering:ActData.Temp.HeatingStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[1] | Var | 10.168.100.10 | Actual Temperature Heating Stage | tt_150_actual_temp_heating_stage
6 | [TT100]Tempering:ActData.Temp.WaterHeatStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[2] | Var | 10.168.100.10 | Actual Temperature Water Heat Stage | tt_150_actual_temp_water_heat_stage
7 | [TT100]Tempering:ActData.Temp.ChocHeatStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[3] | Var | 10.168.100.10 | Actual Temperature Chocolate Heat Stage | tt_150_actual_temp_chocolate_heat_stage
8 | [TT100]Tempering:ActData.Temp.WaterCoolStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[4] | Var | 10.168.100.10 | Actual Temperature Water Cool Stage | tt_150_actual_temp_water_cool_stage
9 | [TT100]Tempering:ActData.Temp.ChocCoolStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[5] | Var | 10.168.100.10 | Actual Temperature Chocolate Cool Stage | tt_150_actual_temp_choc_cool_stage
10 | [TT100]Tempering:ActData.Temp.WaterMixStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[6] | Var | 10.168.100.10 | Actual Temperature Water Mix Stage | tt_150_actual_temp_water_mix_stage
11 | [TT100]Tempering:ActData.Temp.ChocMixstage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[7] | Var | 10.168.100.10 | Actual Temperature Chocolate Mix Stage | tt_150_actual_temp_choc_mix_stage
12 | [TT100]Tempering:ActData.Temp.WaterChocPipe | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[8] | Var | 10.168.100.10 | Actual Temperature Water Chocolate Pipe | tt_150_actual_temp_water_choc_pipe
13 | [TT100]Tempering:ActData.Data.ChocPressure | [Skynet]ComData_TT_100_Alpha_to_Skynet.Process_Values[9] | Var | 10.168.100.10 | Actual Pump Discharge Pressure | tt_150_actual_pump_discharge_pressure
Setpoint Values
14 | [TT100]Tempering:Setpoints.Temp.ChocolateInfeed | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[0] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Infeed | tt_150_setpoint_temp_chocolate_infeed
15 | [TT100]Tempering:Setpoints.Temp.HeatingStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[1] | Var | 10.168.100.10 | Setpoint Temperature Heating Stage | tt_150_setpoint_temp_heating_stage
16 | [TT100]Tempering:Setpoints.Temp.WaterHeatStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[2] | Var | 10.168.100.10 | Setpoint Temperature Water Heat Stage | tt_150_setpoint_temp_water_heat_stage
17 | [TT100]Tempering:Setpoints.Temp.ChocHeatStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[3] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Heat Stage | tt_150_setpoint_temp_chocolate_heat_stage
18 | [TT100]Tempering:Setpoints.Temp.WaterCoolStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[4] | Var | 10.168.100.10 | Setpoint Temperature Water Cool Stage | tt_150_setpoint_temp_water_cool_stage_
19 | [TT100]Tempering:Setpoints.Temp.ChocCoolStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[5] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Cool Stage | tt_150_setpoint_temp_choc_cool_stage
20 | [TT100]Tempering:Setpoints.Temp.WaterMixStage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[6] | Var | 10.168.100.10 | Setpoint Temperature Water Mix Stage | tt_150_setpoint_temp_water_mix_stage
21 | [TT100]Tempering:Setpoints.Temp.ChocMixstage | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[7] | Var | 10.168.100.10 | Setpoint Temperature Chocolate Mix Stage | tt_150_setpoint_temp_choc_mix_stage
22 | [TT100]Tempering:Setpoints.Temp.WaterChocPipe | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[8] | Var | 10.168.100.10 | Setpoint Temperature Water Chocolate Pipe | tt_150_setpoint_temp_water_choc_pipe
23 | [TT100]Tempering:Setpoints.Speeds.FeedPump | [Skynet]ComData_TT_100_Alpha_to_Skynet.Setpoint_Values[9] | Var | 10.168.100.10 | Setpoint Feed Pump (kg/hr) | tt_150_setpoint_feed_pump_kg_hr

## Alpha MT 045
HMI Fault Messages: No Connection Infrastructure Yet
Alarm | Tag name | Value | Path IP | Message
1 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 1 |  | Temperature low
2 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 2 |  | Spare MTAddFault bit 1
3 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 3 |  | Control Voltage 24VDC
4 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 4 |  | High Pressure Compressor
5 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 5 |  | Spare MTAddFault bit 4
6 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 6 |  | Spare MTAddFault bit 5
7 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 7 |  | Spare MTAddFault bit 6
8 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 8 |  | Spare MTAddFault bit 7
9 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 9 |  | Spare MTAddFault bit 8
10 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 10 |  | Spare MTAddFault bit 10
11 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 11 |  | Temperature deviation Water tank
12 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 12 |  | Temperature deviation Chocolate
13 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 13 |  | Spare MTAddFault bit 12
14 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 14 |  | Spare MTAddFault bit 13
15 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 15 |  | Spare MTAddFault bit 14
16 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 16 |  | Spare MTAddFault bit 15
17 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 17 |  | Spare MTAddFault bit 16
18 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 18 |  | Spare MTAddFault bit 17
19 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 19 |  | Spare MTAddFault bit 18
20 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 20 |  | Spare MTAddFault bit 19
21 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 21 |  | Spare MTAddFault bit 20
22 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 22 |  | Spare MTAddFault bit 21
23 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 23 |  | Spare MTAddFault bit 22
24 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 24 |  | Spare MTAddFault bit 23
25 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 25 |  | Spare MTAddFault bit 24
26 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 26 |  | Spare MTAddFault bit 25
27 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 27 |  | Spare MTAddFault bit 26
28 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 28 |  | Spare MTAddFault bit 27
29 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 29 |  | Spare MTAddFault bit 28
30 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 30 |  | Spare MTAddFault bit 29
31 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 31 |  | Spare MTAddFault bit 30
32 | [AP1]Program:AP1_MiniTemper.Fault.MTAddFault | 32 |  | Spare MTAddFault bit 31
33 | [AP1]Program:AP1_MiniTemper.Fault.Tempering | 1 |  | Tempering
34 | [AP1]Program:AP1_MiniTemper.Fault.Enable | 1 |  | Enable
35 | [AP1]Program:AP1_MiniTemper.Fault.bit02 | 1 |  | bit03
36 | [AP1]Program:AP1_MiniTemper.Fault.bit03 | 1 |  | bit04
37 | [AP1]Program:AP1_MiniTemper.Fault.bit04 | 1 |  | bit05
38 | [AP1]Program:AP1_MiniTemper.Fault.bit05 | 1 |  | bit06
39 | [AP1]Program:AP1_MiniTemper.Fault.Stirrer | 1 |  | Stirrer
40 | [AP1]Program:AP1_MiniTemper.Fault.Sieve | 1 |  | Sieve
41 | [AP1]Program:AP1_MiniTemper.Fault.Compressor | 1 |  | Compressor
42 | [AP1]Program:AP1_MiniTemper.Fault.bit09 | 1 |  | bit10
43 | [AP1]Program:AP1_MiniTemper.Fault.bit10 | 1 |  | bit11
44 | [AP1]Program:AP1_MiniTemper.Fault.RefillPumpAuto | 1 |  | Refill
45 | [AP1]Program:AP1_MiniTemper.Fault.RefillPumpMan | 1 |  | RefillPumpMan
46 | [AP1]Program:AP1_MiniTemper.Fault.bit13 | 1 |  | bit14
47 | [AP1]Program:AP1_MiniTemper.Fault.bit14 | 1 |  | bit15
48 | [AP1]Program:AP1_MiniTemper.Fault.bit15 | 1 |  | bit16
49 | [AP1]Program:AP1_MiniTemper.Fault.bit16 | 1 |  | bit17
50 | [AP1]Program:AP1_MiniTemper.Fault.bit17 | 1 |  | bit18
51 | [AP1]Program:AP1_MiniTemper.Fault.bit18 | 1 |  | bit19
52 | [AP1]Program:AP1_MiniTemper.Fault.bit19 | 1 |  | bit20
53 | [AP1]Program:AP1_MiniTemper.Fault.bit20 | 1 |  | bit21
54 | [AP1]Program:AP1_MiniTemper.Fault.bit21 | 1 |  | bit22
55 | [AP1]Program:AP1_MiniTemper.Fault.bit22 | 1 |  | bit23
56 | [AP1]Program:AP1_MiniTemper.Fault.bit23 | 1 |  | bit24
57 | [AP1]Program:AP1_MiniTemper.Fault.bit24 | 1 |  | bit25
58 | [AP1]Program:AP1_MiniTemper.Fault.bit25 | 1 |  | bit26
59 | [AP1]Program:AP1_MiniTemper.Fault.bit26 | 1 |  | bit27
60 | [AP1]Program:AP1_MiniTemper.Fault.bit27 | 1 |  | bit28
61 | [AP1]Program:AP1_MiniTemper.Fault.bit28 | 1 |  | bit29
62 | [AP1]Program: AP1_MiniTemper.Fault.bit29 | 1 |  | bit30
63 | [AP1]Program:AP1_MiniTemper.Fault.bit30 | 1 |  | bit31
64 | [AP1]Program: AP1_MiniTemper.Fault.bit31 | 1 |  | bit32

## Alpha DBS 080
HMI Fault Messages:
# | Component | Fault Value | Error Text | Description
| SM_Ctr_Main | 1001000 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
| SM_Ctr_Main | 1001001 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
| SM_Ctr_Main | 1001002 | Too small | This is a system failure: the shown registration list is too small.
| SM_Ctr_Main | 1001003 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
| SM_Ctr_Main | 1001004 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
| SM_Ctr_Main | 1001005 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
| SM_Ctr_Main | 1001006 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
| SM_Ctr_Main | 1001007 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
| SM_Ctr_Main | 1001008 | Controller Timeout | Global Statemachine fault.
| SM_Ctr_Main | 1001009 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
| SM_Ctr_Main | 1001010 | State machine init - | This is a system failure.
| SM_Ctr_Main | 1001011 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
| SM_Ctr_Main | 1001012 | No connection to drive (s) | When this alarm is displayed, the connection to one, or more drives, is suspended.
| HMI_Main | 1002000 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| (PLC1_)CPU_Main | 1003000 | Battery low | The voltage of the internal battery of the PLC is low.
| (PLC1_)CPU_Main | 1003005 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout.
| GMS_Main | 1004000 | Circuit breaker transformer control voltage | The circuit breaker is switched off.
| GMS_Main | 1004001 | Circuit breaker drive Power supply | The circuit breaker is switched off.
| IO_Main | 1005001 | Electronic fuse triggered on 2A digital output card | The electronic protection circuit of one the of digital output cards for 2A high power outputs of the PLC has been activated due to a short circuit.
| IO_Main | 1005012 | BLTHOL: Missing remote I/O | One of the Remote I/O modules is missing.
| IO_Main | 1005013 | DDU1: Missing remote I/O | One of the Remote I/O modules is missing.
| IO_Main | 1005020 | DU1: Missing remote I/O | One of the Remote I/O modules is missing.
| IO_Main | 1005021 | DU2: Missing remote I/O | One of the Remote I/O modules is missing.
| IO_Main | 1005022 | DU3: Missing remote I/O | One of the Remote I/O modules is missing.
| IO_Main | 1005023 | DU4: Missing remote I/O | One of the Remote I/O modules is missing.
| IO_Main | 1005024 | DU5: Missing remote I/O | One of the Remote I/O modules is missing.
| IO_Main | 1005029 | DUR: Missing remote I/O | One of the Remote I/O modules is missing.
| SAF_Main | 1020006 | LOTO switch main cabinet turned off | The Lock Out Tag Out (LOTO) switch at main cabinet is turned off.
| SFT_SAF | 1020010 | Emergency stop customer | The emergency stop button from customer is pressed or has already been disengaged.
| SFT_SAF | 1020011 | Emergency stop ALN1 left | The emergency stop button at the aligner 1 is pressed or has already been disengaged.
| SFT_SAF | 1020012 | Emergency stop ALN1 right | The emergency stop button at the aligner 1 is pressed or has already been disengaged.
| SFT_SAF | 1020013 | Emergency stop ALN2 left | The emergency stop button at the aligner 2 is pressed or has already been disengaged.
| SFT_SAF | 1020014 | Emergency stop ALN2 right | The emergency stop button at the aligner 2 is pressed or has already been disengaged.
| SFT_SAF | 1020015 | Emergency stop BLTHOL U3 left | The emergency stop button at the BLTHOL U3 belt is pressed or has already been disengaged.
| SFT_SAF | 1020016 | Emergency stop BLTHOL U3 right | The emergency stop button at the BLTHOL U3 belt is pressed or has already been disengaged.
| SFT_SAF | 1020017 | Emergency stop ALN3 left | The emergency stop button at the aligner 3 is pressed or has already been disengaged.
| SFT_SAF | 1020018 | Emergency stop ALN3 right | The emergency stop button at the aligner 3 is pressed or has already been disengaged.
| SFT_SAF | 1020019 | Emergency stop DDU1 left | The emergency stop button at the dump unit 1 is pressed or has already been disengaged.
| SFT_SAF | 1020020 | Emergency stop DDU1 right | The emergency stop button at the dump unit 1 is pressed or has already been disengaged.
| SFT_SAF | 1020021 | Emergency stop DU1 left | The emergency stop button at the distribution unit 1 is pressed or has already been disengaged.
| SFT_SAF | 1020022 | Emergency stop DU1 right | The emergency stop button at the distribution unit 1 is pressed or has already been disengaged.
| SFT_SAF | 1020023 | Emergency stop DU2 left | The emergency stop button at the distribution unit 2 is pressed or has already been disengaged.
| SFT_SAF | 1020024 | Emergency stop DU2 right | The emergency stop button at the distribution unit 2 is pressed or has already been disengaged.
| SFT_SAF | 1020025 | Emergency stop DU3 left | The emergency stop button at the distribution unit 3 is pressed or has already been disengaged.
| SFT_SAF | 1020026 | Emergency stop DU3 right | The emergency stop button at the distribution unit 3 is pressed or has already been disengaged.
| SFT_SAF | 1020027 | Emergency stop DU4 left | The emergency stop button at the distribution unit 4 is pressed or has already been disengaged.
| SFT_SAF | 1020028 | Emergency stop DU4 right | The emergency stop button at the distribution unit 4 is pressed or has already been disengaged.
| SFT_SAF | 1020029 | Emergency stop DU5 left | The emergency stop button at the distribution unit 5 is pressed or has already been disengaged.
| SFT_SAF | 1020030 | Emergency stop DU5 right | The emergency stop button at the distribution unit 5 is pressed or has already been disengaged.
| SFT_SAF | 1020031 | Emergency stop DUR left | The emergency stop button at the refeed distribution unit is pressed or has already been disengaged.
| SFT_SAF | 1020032 | Emergency stop DUR right | The emergency stop button at the refeed distribution unit is pressed or has already been disengaged.
| SFT_SAF | 1020033 | Emergency stop RBLT left | The emergency stop button at the refeed belt is pressed or has already been disengaged.
| SFT_SAF | 1020034 | Emergency stop RBLT right | The emergency stop button at the refeed belt is pressed or has already been disengaged.
| UIFACE_Main | 1030000 | Upstream interface disabled | The upstream interface is disabled.
| UIFACE_Main | 1030002 | Communication loss with upstream PLC | The communication to the upstream PLC is disturbed.
| DIFACE_Main | 1031000 | Downstream interface disabled | The downstream interface is disabled.
| DIFACE_Main | 1031002 | Communication loss with downstream PLC | The communication to the downstream PLC is disturbed.
| DIFACE_Main | 1031003 | Accu not ready | Infeed at downstream buffer is not ready
| DIFACE_Main | 1031004 | Accu nearly full | The downstream buffer is nearly full
| RAPID_Main | 1052000 | Suspend from RAPID Line Controller | Equipment has been suspended by RAPID Line Controller.
| RAPID_Main | 1052001 | Stop or Hold from RAPID Line Controller | Equipment has been stopped by RAPID Line Controller by a hold/stop command.
| RAPID_Main | 1052002 | RAPID Line Controller commands switched off | Equipment will not react to RAPID Line Controller commands.
| (PLC2_)SM_Ctr_Main | 2001000 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
| (PLC2_)SM_Ctr_Main | 2001001 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
| (PLC2_)SM_Ctr_Main | 2001002 | Too small | This is a system failure: the shown registration list is too small.
| (PLC2_)SM_Ctr_Main | 2001003 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
| (PLC2_)SM_Ctr_Main | 2001004 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
| (PLC2_)SM_Ctr_Main | 2001005 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
| (PLC2_)SM_Ctr_Main | 2001006 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
| (PLC2_)SM_Ctr_Main | 2001007 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
| (PLC2_)SM_Ctr_Main | 2001008 | Controller Timeout | Global Statemachine fault.
| (PLC2_)SM_Ctr_Main | 2001009 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
| (PLC2_)SM_Ctr_Main | 2001010 | State machine init - | This is a system failure.
| (PLC2_)SM_Ctr_Main | 2001011 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
| (PLC2_)CPU_Main | 2003000 | Battery low | The voltage of the internal battery of the PLC is low.
| (PLC2_)CPU_Main | 2003005 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout.
| ALN1_SM_Main | 11010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| ALN1_SM_Main | 11010001 | Service mode active | The aligner is in service mode. No aligning possible.
| ALN1_SM_Main | 11010002 | Calculation active | The unit is in calculation state.
| ALN1_SM_Main | 11010003 | Switched off | The aligner is disabled.
| ALN1_SM_Main | 11010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| SFT_ALN1_Saf | 11020010 | cover open | There is a guard on the machine which is open.
| ALN1_Saf_Cov | 11020018 | cover open requested | The guard will be open if the last move is done.
| SFT_ALN1_Saf | 11020060 | Energize drive fault | The energizing of the drive is faulted.
| ALN1_Saf_Air_MS6SV | 11020090 | Exhaust valve fault | The exhaust valve has a fault.
| ALN1_Saf_Air_MS6SV | 11020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_ALN1_Saf | 11020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| ALN1_Saf_Air_HEED | 11020093 | Air pressure too low | The air pressure is below the allowed operating level.
| ALN1_Saf_Air_HEED | 11020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| ALN1_Ax_Main | 11200000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| ALN1_Ax_Main | 11200001 | Position error | The controlled motor is out of the commanded position.
| ALN1_Ax_Main | 11200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| ALN1_Ax_Main | 11200003 | Validation error | This is a validation error. One of the values is out of range.
| ALN1_Ax_Main | 11200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| ALN1_Ax_Main | 11200010 | Acc / Dec out of range | This is a validation error. Acceleration / deceleration out of range (bigger than maximum, or less than the minimum required to decelerate after aligning into the open position).
| ALN1_Ax_Main | 11200011 | Cycle time of the aligner too long | This is a validation error. The aligner needs too long for a cycle. Increase speeds and acc/dec to speed-up the aligner.
| ALN1_Ax_Main | 11200012 | Wrong aligner distance | This is a validation error. The aligner is too close to its start position.
| ALN1_Ax_Main | 11200013 | End move is too fast | This is a validation error. If the option clever aligning is on we have to move into the gap directly - without waiting in the open position. If the last move is too fast we would touch the rear edge of the row.
| ALN1_Ax_Main | 11200014 | Adjustment error | This is an adjustment error. One of the values is out of range.
| ALN1_Ax_Main | 11200016 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN1_Ax_Main | 11200017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN1_Ax_Main | 11200018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| ALN1_Ax_Main | 11200019 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| ALN1_Ax_Main | 11200020 | Home needed | The aligner is stopping to home after restart.
| ALN1_Ax_Main | 11200021 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| ALN1_Ax_Main | 11200022 | Product too high | There is a too high product detected in front of the aligner.
| ALN1_Ax_Main | 11200023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| ALN1_Pneum_Main | 11201004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| ALN1_Pneum_Main | 11201016 | Warning photoeye is not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN1_Pneum_Main | 11201017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN1_Pneum_Main | 11201018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| ALN2_SM_Main | 12010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| ALN2_SM_Main | 12010001 | Service mode active | The aligner is in service mode. No aligning possible.
| ALN2_SM_Main | 12010002 | Calculation active | The unit is in calculation state.
| ALN2_SM_Main | 12010003 | Switched off | The aligner is disabled.
| ALN2_SM_Main | 12010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| SFT_ALN2_Saf | 12020010 | cover open | There is a guard on the machine which is open.
| ALN2_Saf_Cov | 12020018 | cover open requested | The guard will be open if the last move is done.
| SFT_ALN2_Saf | 12020060 | Energize drive fault | The energizing of the drive is faulted.
| ALN2_Saf_Air_MS6SV | 12020090 | Exhaust valve fault | The exhaust valve has a fault.
| ALN2_Saf_Air_MS6SV | 12020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_ALN2_Saf | 12020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| ALN2_Saf_Air_HEED | 12020093 | Air pressure too low | The air pressure is below the allowed operating level.
| ALN2_Saf_Air_HEED | 12020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| ALN2_Ax_Main | 12200000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| ALN2_Ax_Main | 12200001 | Position error | The controlled motor is out of the commanded position.
| ALN2_Ax_Main | 12200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| ALN2_Ax_Main | 12200003 | Validation error | This is a validation error. One of the values is out of range.
| ALN2_Ax_Main | 12200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| ALN2_Ax_Main | 12200010 | Acc / Dec out of range | This is a validation error. Acceleration / deceleration out of range (bigger than maximum, or less than the minimum required to decelerate after aligning into the open position).
| ALN2_Ax_Main | 12200011 | Cycle time of the aligner too long | This is a validation error. The aligner needs too long for a cycle. Increase speeds and acc/dec to speed-up the aligner.
| ALN2_Ax_Main | 12200012 | Wrong aligner distance | This is a validation error. The aligner is too close to its start position.
| ALN2_Ax_Main | 12200013 | End move is too fast | This is a validation error. If the option clever aligning is on we have to move into the gap directly - without waiting in the open position. If the last move is too fast we would touch the rear edge of the row.
| ALN2_Ax_Main | 12200014 | Adjustment error | This is an adjustment error. One of the values is out of range.
| ALN2_Ax_Main | 12200016 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN2_Ax_Main | 12200017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN2_Ax_Main | 12200018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| ALN2_Ax_Main | 12200019 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| ALN2_Ax_Main | 12200020 | Home needed | The aligner is stopping to home after restart.
| ALN2_Ax_Main | 12200021 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| ALN2_Ax_Main | 12200022 | Product too high | There is a too high product detected in front of the aligner.
| ALN2_Ax_Main | 12200023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| ALN2_Pneum_Main | 12201004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| ALN2_Pneum_Main | 12201016 | Warning photoeye is not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN2_Pneum_Main | 12201017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN2_Pneum_Main | 12201018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| ALN3_SM_Main | 13010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| ALN3_SM_Main | 13010001 | Service mode active | The aligner is in service mode. No aligning possible.
| ALN3_SM_Main | 13010002 | Calculation active | The unit is in calculation state.
| ALN3_SM_Main | 13010003 | Switched off | The aligner is disabled.
| ALN3_SM_Main | 13010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| SFT_ALN3_Saf | 13020010 | cover open | There is a guard on the machine which is open.
| ALN3_Saf_Cov | 13020018 | cover open requested | The guard will be open if the last move is done.
| SFT_ALN3_Saf | 13020060 | Energize drive fault | The energizing of the drive is faulted.
| ALN3_Saf_Air_MS6SV | 13020090 | Exhaust valve fault | The exhaust valve has a fault.
| ALN3_Saf_Air_MS6SV | 13020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_ALN3_Saf | 13020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| ALN3_Saf_Air_HEED | 13020093 | Air pressure too low | The air pressure is below the allowed operating level.
| ALN3_Saf_Air_HEED | 13020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| ALN3_Ax_Main | 13200000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| ALN3_Ax_Main | 13200001 | Position error | The controlled motor is out of the commanded position.
| ALN3_Ax_Main | 13200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| ALN3_Ax_Main | 13200003 | Validation error | This is a validation error. One of the values is out of range.
| ALN3_Ax_Main | 13200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| ALN3_Ax_Main | 13200010 | Acc / Dec out of range | This is a validation error. Acceleration / deceleration out of range (bigger than maximum, or less than the minimum required to decelerate after aligning into the open position).
| ALN3_Ax_Main | 13200011 | Cycle time of the aligner too long | This is a validation error. The aligner needs too long for a cycle. Increase speeds and acc/dec to speed-up the aligner.
| ALN3_Ax_Main | 13200012 | Wrong aligner distance | This is a validation error. The aligner is too close to its start position.
| ALN3_Ax_Main | 13200013 | End move is too fast | This is a validation error. If the option clever aligning is on we have to move into the gap directly - without waiting in the open position. If the last move is too fast we would touch the rear edge of the row.
| ALN3_Ax_Main | 13200014 | Adjustment error | This is an adjustment error. One of the values is out of range.
| ALN3_Ax_Main | 13200016 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN3_Ax_Main | 13200017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN3_Ax_Main | 13200018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| ALN3_Ax_Main | 13200019 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| ALN3_Ax_Main | 13200020 | Home needed | The aligner is stopping to home after restart.
| ALN3_Ax_Main | 13200021 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| ALN3_Ax_Main | 13200022 | Product too high | There is a too high product detected in front of the aligner.
| ALN3_Ax_Main | 13200023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| ALN3_Pneum_Main | 13201004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| ALN3_Pneum_Main | 13201016 | Warning photoeye is not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN3_Pneum_Main | 13201017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| ALN3_Pneum_Main | 13201018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DBP_SM_Main | 15010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DBP_SM_Main | 15010001 | Service mode active | The unit is in service mode. No production active.
| DBP_SM_Main | 15010002 | Calculation active | The unit is in calculation state.
| DBP_SM_Main | 15010003 | Unit switched off | The unit is disabled.
| DBP_SM_Main | 15010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| DBP_AxPuln_Main | 15200000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DBP_AxPuln_Main | 15200001 | Position error | The controlled motor is out of the commanded position.
| DBP_AxPuln_Main | 15200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DBP_AxPuln_Main | 15200003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DBP_AxPuln_Main | 15200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DBP_AxPuln_Main | 15200006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
| DBP_AxPuln_Main | 15200010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DBP_AxPuln_Main | 15200011 | Negative overtravel | The axis has exceeded the software limit position in negative direction.
| DBP_AxPuln_Main | 15200012 | Positive overtravel | The axis has exceeded the software limit position in positive direction.
| DBP_AxPuln_Main | 15200014 | Adjustment error | This is an adjustment error. One of the values is out of range.
| DBP_AxPuln_Main | 15200017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
| DBP_AxPuln_Main | 15200018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| BLTHOL_SM_Main | 17010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| BLTHOL_SM_Main | 17010001 | Service mode active | The process belts are in service mode. No production possible
| BLTHOL_SM_Main | 17010002 | Calculation active | The unit is in calculation state.
| BLTHOL_SM_Main | 17010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| BLTHOL_SM_Main | 17010005 | Clean mode belts active | The process belts are in clean mode. No production possible.
| BLTHOL_SM_Main | 17010006 | Empty mode belts is active | The belt empty mode is active.
| SFT_BLTHOL_Saf | 17020060 | Energize drive fault BLTHOL U1 belt | The energizing of the drive is faulted.
| SFT_BLTHOL_Saf | 17020061 | Energize drive fault BLTHOL U2 belt | The energizing of the drive is faulted.
| SFT_BLTHOL_Saf | 17020062 | Energize drive fault BLTHOL U3 belt | The energizing of the drive is faulted.
| SFT_BLTHOL_Saf | 17020063 | Energize drive fault BLTHOL U4 belt | The energizing of the drive is faulted.
| SFT_BLTHOL_Saf | 17020065 | Energize drive fault BLTHOL Ddu1 belt | The energizing of the drive is faulted.
| SFT_BLTHOL_Saf | 17020066 | Energize drive fault BLTHOL Ddu1 Ev belt | The energizing of the drive is faulted.
| SFT_BLTHOL_Saf | 17020070 | Energize drive fault belt track HOL belts | The energizing of the belt track drive is faulted.
| BLTHOL_Saf_Air_MS6SV | 17020090 | Exhaust valve fault | The exhaust valve has a fault.
| BLTHOL_Saf_Air_MS6SV | 17020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_BLTHOL_Saf | 17020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| BLTHOL_Saf_Air_HEED | 17020093 | Air pressure too low | The air pressure is below the allowed operating level.
| BLTHOL_Saf_Air_HEED | 17020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| BLTHOL_Ctr_Main | 17100000 | Downstream equipment not ready | The downstream equipment is not ready.
| BLTHOL_Ctr_Main | 17100001 | Empty belts active until DDU1 | Upstream is not ready. No product is coming in from upstream.
| BLTHOL_Ctr_Main | 17100999 | Not displayed on HMI!
| RR1_AxBlt_Main | 17105000 | Drive fault | There is a fault on this drive.
| RR1_AxBlt_Main | 17105001 | Position error | The controlled motor is out of the commanded position.
| RR1_AxBlt_Main | 17105002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| RR1_AxBlt_Main | 17105003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| RR1_AxBlt_Main | 17105004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| RR1_AxBlt_Main | 17105010 | Photoeye row detection is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| RR1_AxBlt_Main | 17105011 | Adjustment fault | There is a functional fault. It is not possible to do the commanded function of the row regulation belt due to bad parameter settings.
| RR1_BltTrack_Main | 17107000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| RR1_BltTrack_Main | 17107001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| RR1_BltTrack_Servo | 17107002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| RR1_BltTrack_Servo | 17107003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| RR1_BltTrack_Servo | 17107004 | Cylinder homing active | The cylinder is homing
| RR1_BltTrack_Servo | 17107005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| RR2_AxBlt_Main | 17110000 | Drive fault | There is a fault on this drive.
| RR2_AxBlt_Main | 17110001 | Position error | The controlled motor is out of the commanded position.
| RR2_AxBlt_Main | 17110002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| RR2_AxBlt_Main | 17110003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| RR2_AxBlt_Main | 17110004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| RR2_AxBlt_Main | 17110010 | Photoeye row detection is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| RR2_AxBlt_Main | 17110011 | Adjustment fault | There is a functional fault. It is not possible to do the commanded function of the row regulation belt due to bad parameter settings.
| RR2_BltTrack_Main | 17112000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| RR2_BltTrack_Main | 17112001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| RR2_BltTrack_Servo | 17112002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| RR2_BltTrack_Servo | 17112003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| RR2_BltTrack_Servo | 17112004 | Cylinder homing active | The cylinder is homing
| RR2_BltTrack_Servo | 17112005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLTHOL_AxU1_Main | 17200000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxU1_Main | 17200001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxU1_Main | 17200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxU1_Main | 17200003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxU1_Main | 17200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxU1_Main | 17200012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_U1Track_Main | 17201000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U1Track_Main | 17201001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U1Track_Servo | 17201002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLTHOL_U1Track_Servo | 17201003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLTHOL_U1Track_Servo | 17201004 | Cylinder homing active | The cylinder is homing
| BLTHOL_U1Track_Servo | 17201005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLTHOL_AxU1Left_Main | 17203000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxU1Left_Main | 17203001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxU1Left_Main | 17203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxU1Left_Main | 17203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxU1Left_Main | 17203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxU1Left_Main | 17203012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_AxU1Right_Main | 17204000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxU1Right_Main | 17204001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxU1Right_Main | 17204002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxU1Right_Main | 17204003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxU1Right_Main | 17204004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxU1Right_Main | 17204012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_AxU2_Main | 17210000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxU2_Main | 17210001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxU2_Main | 17210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxU2_Main | 17210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxU2_Main | 17210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxU2_Main | 17210012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_U2Track_Main | 17211000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U2Track_Main | 17211001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U2Track_Servo | 17211002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLTHOL_U2Track_Servo | 17211003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLTHOL_U2Track_Servo | 17211004 | Cylinder homing active | The cylinder is homing
| BLTHOL_U2Track_Servo | 17211005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLTHOL_AxU3_Main | 17220000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxU3_Main | 17220001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxU3_Main | 17220002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxU3_Main | 17220003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxU3_Main | 17220004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxU3_Main | 17220012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_U3Track_Main | 17221000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U3Track_Main | 17221001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U3Track_Servo | 17221002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLTHOL_U3Track_Servo | 17221003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLTHOL_U3Track_Servo | 17221004 | Cylinder homing active | The cylinder is homing
| BLTHOL_U3Track_Servo | 17221005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLTHOL_AxU4_Main | 17230000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxU4_Main | 17230001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxU4_Main | 17230002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxU4_Main | 17230003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxU4_Main | 17230004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxU4_Main | 17230012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_U4Track_Main | 17231000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U4Track_Main | 17231001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_U4Track_Servo | 17231002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLTHOL_U4Track_Servo | 17231003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLTHOL_U4Track_Servo | 17231004 | Cylinder homing active | The cylinder is homing
| BLTHOL_U4Track_Servo | 17231005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLTHOL_AxDdu1_Main | 17400000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxDdu1_Main | 17400001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxDdu1_Main | 17400002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxDdu1_Main | 17400003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxDdu1_Main | 17400004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxDdu1_Main | 17400012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_Ddu1Track_Main | 17401000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_Ddu1Track_Main | 17401001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLTHOL_Ddu1Track_Servo | 17401002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLTHOL_Ddu1Track_Servo | 17401003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLTHOL_Ddu1Track_Servo | 17401004 | Cylinder homing active | The cylinder is homing
| BLTHOL_Ddu1Track_Servo | 17401005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLTHOL_AxDdu1Left_Main | 17403000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxDdu1Left_Main | 17403001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxDdu1Left_Main | 17403002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxDdu1Left_Main | 17403003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxDdu1Left_Main | 17403004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxDdu1Left_Main | 17403012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_AxDdu1Right_Main | 17404000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxDdu1Right_Main | 17404001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxDdu1Right_Main | 17404002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxDdu1Right_Main | 17404003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxDdu1Right_Main | 17404004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLTHOL_AxDdu1Right_Main | 17404012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLTHOL_AxDdu1Ev_Main | 17405000 | Drive fault | There is a fault on this drive.
| BLTHOL_AxDdu1Ev_Main | 17405001 | Position error | The controlled motor is out of the commanded position.
| BLTHOL_AxDdu1Ev_Main | 17405002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLTHOL_AxDdu1Ev_Main | 17405003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLTHOL_AxDdu1Ev_Main | 17405004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_SM_Main | 18010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| BLT_SM_Main | 18010001 | Service mode active | The process belts are in service mode. No production possible
| BLT_SM_Main | 18010002 | Calculation active | The unit is in calculation state.
| BLT_SM_Main | 18010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| BLT_SM_Main | 18010005 | Clean mode belts active | The process belts are in clean mode. No production possible.
| BLT_SM_Main | 18010006 | Empty mode belts is active | The belt empty mode is active.
| SFT_BLT_Saf | 18020060 | Energize drive fault BLT DU1 | The energizing of the drive is faulted.
| SFT_BLT_Saf | 18020061 | Energize drive fault BLT DU2 | The energizing of the drive is faulted.
| SFT_BLT_Saf | 18020062 | Energize drive fault BLT DUR | The energizing of the drive is faulted.
| SFT_BLT_Saf | 18020063 | Energize drive fault R-Belt | The energizing of the drive is faulted.
| SFT_BLT_Saf | 18020070 | Energize drives fault belt track DU1 / Ux | The energizing of the belt track drive is faulted.
| SFT_BLT_Saf | 18020071 | Energize drives fault belt track DUR / Rbelt | The energizing of the belt track drive is faulted.
| BLT_Saf_Air_MS6SV | 18020090 | Exhaust valve fault | The exhaust valve has a fault.
| BLT_Saf_Air_MS6SV | 18020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_BLT_Saf | 18020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| BLT_Saf_Air_HEED | 18020093 | Air pressure too low | The air pressure is below the allowed operating level.
| BLT_Saf_Air_HEED | 18020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| BLT_Ctr_Main | 18100000 | Downstream equipment not ready | The downstream equipment is not ready.
| BLT_Ctr_Main | 18100001 | Empty belts active until last DUX | Upstream is not ready. No product is coming in from upstream.
| BLT_Ctr_Main | 18100002 | Production stopped - main belts stopped | Upstream is not ready. No product is coming in from upstream.
| BLT_Ctr_Main | 18100999 | Not displayed on HMI!
| BLT_DumpVer_Main | 18110000 | Too many rows in register | There are too many rows between the belt edge and the verification photoeye.
| BLT_AxU1_Main | 18200000 | Drive fault | There is a fault on this drive.
| BLT_AxU1_Main | 18200001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxU1_Main | 18200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxU1_Main | 18200003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxU1_Main | 18200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxU1_Main | 18200012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_U1Track_Main | 18201000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U1Track_Main | 18201001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U1Track_Servo | 18201002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_U1Track_Servo | 18201003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_U1Track_Servo | 18201004 | Cylinder homing active | The cylinder is homing
| BLT_U1Track_Servo | 18201005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxU1Left_Main | 18203000 | Drive fault | There is a fault on this drive.
| BLT_AxU1Left_Main | 18203001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxU1Left_Main | 18203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxU1Left_Main | 18203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxU1Left_Main | 18203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxU1Left_Main | 18203012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_AxU1Right_Main | 18204000 | Drive fault | There is a fault on this drive.
| BLT_AxU1Right_Main | 18204001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxU1Right_Main | 18204002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxU1Right_Main | 18204003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxU1Right_Main | 18204004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxU1Right_Main | 18204012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_AxU2_Main | 18210000 | Drive fault | There is a fault on this drive.
| BLT_AxU2_Main | 18210001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxU2_Main | 18210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxU2_Main | 18210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxU2_Main | 18210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxU2_Main | 18210012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_U2Track_Main | 18211000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U2Track_Main | 18211001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U2Track_Servo | 18211002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_U2Track_Servo | 18211003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_U2Track_Servo | 18211004 | Cylinder homing active | The cylinder is homing
| BLT_U2Track_Servo | 18211005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxU3_Main | 18220000 | Drive fault | There is a fault on this drive.
| BLT_AxU3_Main | 18220001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxU3_Main | 18220002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxU3_Main | 18220003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxU3_Main | 18220004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxU3_Main | 18220012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_U3Track_Main | 18221000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U3Track_Main | 18221001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U3Track_Servo | 18221002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_U3Track_Servo | 18221003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_U3Track_Servo | 18221004 | Cylinder homing active | The cylinder is homing
| BLT_U3Track_Servo | 18221005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxU4_Main | 18230000 | Drive fault | There is a fault on this drive.
| BLT_AxU4_Main | 18230001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxU4_Main | 18230002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxU4_Main | 18230003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxU4_Main | 18230004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxU4_Main | 18230012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_U4Track_Main | 18231000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U4Track_Main | 18231001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_U4Track_Servo | 18231002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_U4Track_Servo | 18231003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_U4Track_Servo | 18231004 | Cylinder homing active | The cylinder is homing
| BLT_U4Track_Servo | 18231005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxDu1_Main | 18500000 | Drive fault | There is a fault on this drive.
| BLT_AxDu1_Main | 18500001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxDu1_Main | 18500002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxDu1_Main | 18500003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxDu1_Main | 18500004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxDu1_Main | 18500012 | An element on belt is not ready | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_AxDu1_Main | 18500015 | Bad (metal) row was not rejected | The supervision of the dump unit has detected a row that should have been dumped.
| BLT_Du1Track_Main | 18501000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du1Track_Main | 18501001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du1Track_Main | 18501002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_Du1Track_Main | 18501003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_Du1Track_Main | 18501004 | Cylinder homing active | The cylinder is homing
| BLT_Du1Track_Main | 18501005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxDu2_Main | 18510000 | Drive fault | There is a fault on this drive.
| BLT_AxDu2_Main | 18510001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxDu2_Main | 18510002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxDu2_Main | 18510003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxDu2_Main | 18510004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxDu2_Main | 18510012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_Du2Track_Main | 18511000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du2Track_Main | 18511001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du2Track_Main | 18511002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_Du2Track_Main | 18511003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_Du2Track_Main | 18511004 | Cylinder homing active | The cylinder is homing
| BLT_Du2Track_Main | 18511005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxDu3_Main | 18520000 | Drive fault | There is a fault on this drive.
| BLT_AxDu3_Main | 18520001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxDu3_Main | 18520002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxDu3_Main | 18520003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxDu3_Main | 18520004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxDu3_Main | 18520012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_Du3Track_Main | 18521000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du3Track_Main | 18521001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du3Track_Main | 18521002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_Du3Track_Main | 18521003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_Du3Track_Main | 18521004 | Cylinder homing active | The cylinder is homing
| BLT_Du3Track_Main | 18521005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxDu4_Main | 18530000 | Drive fault | There is a fault on this drive.
| BLT_AxDu4_Main | 18530001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxDu4_Main | 18530002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxDu4_Main | 18530003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxDu4_Main | 18530004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxDu4_Main | 18530012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_Du4Track_Main | 18531000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du4Track_Main | 18531001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du4Track_Main | 18531002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_Du4Track_Main | 18531003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_Du4Track_Main | 18531004 | Cylinder homing active | The cylinder is homing
| BLT_Du4Track_Main | 18531005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxDu5_Main | 18540000 | Drive fault | There is a fault on this drive.
| BLT_AxDu5_Main | 18540001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxDu5_Main | 18540002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxDu5_Main | 18540003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxDu5_Main | 18540004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxDu5_Main | 18540012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_Du5Track_Main | 18541000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du5Track_Main | 18541001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_Du5Track_Main | 18541002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| BLT_Du5Track_Main | 18541003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_Du5Track_Main | 18541004 | Cylinder homing active | The cylinder is homing
| BLT_Du5Track_Main | 18541005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| BLT_AxDuR_Main | 18590000 | Drive fault | There is a fault on this drive.
| BLT_AxDuR_Main | 18590001 | Position error | The controlled motor is out of the commanded position.
| BLT_AxDuR_Main | 18590002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| BLT_AxDuR_Main | 18590003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| BLT_AxDuR_Main | 18590004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| BLT_AxDuR_Main | 18590012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| BLT_DuRTrack_Main | 18591000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_DuRTrack_Main | 18591001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| BLT_DuRTrack_Main | 18591003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| BLT_DuRTrack_Main | 18591004 | Cylinder homing active | The cylinder is homing
| BLT_DuRTrack_Main | 18591005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| RBLT_Ctr_Main | 18600000 | R-Belt is full | The products on the recycling belt have reached the fill level. Check if you can remove products from the belt.
| RBLT_Ctr_Main | 18600001 | Bad aligned row | If the row is too long we move a bigger distance with the rbelt and set a warning for the operator:
| RBLT_Ctr_Main | 18600002 | Manual mode active | The R-Blt has been or is being moved manually with the foot switch. To go back to normal function press the reload foot switch for more than 3 seconds or press the reset button.
| RBLT_Ctr_Main | 18600003 | Photoeye discharge not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| RBLT_AxU1_Main | 18601000 | Drive fault | There is a fault on this drive.
| RBLT_AxU1_Main | 18601001 | Position error | The controlled motor is out of the commanded position.
| RBLT_AxU1_Main | 18601002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| RBLT_AxU1_Main | 18601003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| RBLT_AxU1_Main | 18601004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| RBLT_AxU1_Main | 18601012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
| RBLT_U1Track_Main | 18602000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| RBLT_U1Track_Main | 18602001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| RBLT_U1Track_Servo | 18602002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| RBLT_U1Track_Servo | 18602003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| RBLT_U1Track_Servo | 18602004 | Cylinder homing active | The cylinder is homing
| RBLT_U1Track_Servo | 18602005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| DU1_GMS_Main | 21004000 | Circuit breaker drive control voltage | The circuit breaker is switched off.
| DU1_GMS_Main | 21004001 | Circuit breaker belt tracking control voltage | The circuit breaker is switched off.
| DU1_GMS_Main | 21004002 | Converter fault | The converter is reporting a fault.
| DU1_SM_Main | 21010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DU1_SM_Main | 21010001 | Service mode active | The distribution unit is in service mode. No production active.
| DU1_SM_Main | 21010002 | Calculation active | The unit is in calculation state.
| DU1_SM_Main | 21010003 | Unit switched off | The unit is disabled.
| DU1_SM_Main | 21010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| DU1_SM_Main | 21010005 | Clean mode unit is active | The unit clean mode is active.
| DU1_SM_Main | 21010006 | Deactivated | The distribution unit is deactivated. No new rows will be distributed to the unit. Rows from within the unit will be discharged (the unit will be emptied).
| SFT_DU1_Saf | 21020010 | Door left 1 open | There is a guard on the machine which is open.
| SFT_DU1_Saf | 21020011 | Door left 2 open | There is a guard on the machine which is open.
| SFT_DU1_Saf | 21020012 | Door right 1 open | There is a guard on the machine which is open.
| SFT_DU1_Saf | 21020013 | Door right 2 open | There is a guard on the machine which is open.
| SFT_DU1_Saf | 21020014 | Discharge belt not in working position | The discharge belt is not in working position
| DU1_Saf_Cov | 21020018 | Doors open requested | The guard will be opened as soon as the last move is done.
| SFT_DU1_Saf | 21020060 | Energize drive fault Diverter | The energizing of the drive is faulted.
| SFT_DU1_Saf | 21020061 | Energize drive fault Waitbelt | The energizing of the drive is faulted.
| SFT_DU1_Saf | 21020062 | Energize drive fault Pusher | The energizing of the drive is faulted.
| SFT_DU1_Saf | 21020063 | Energize drive fault Pusher Flap | The energizing of the drive is faulted.
| SFT_DU1_Saf | 21020070 | Energize drive fault belt track Waitbelt | The energizing of the drive is faulted.
| DU1_Saf_Air_MS6SV | 21020090 | Exhaust valve fault | The exhaust valve has a fault.
| DU1_Saf_Air_MS6SV | 21020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_DU1_Saf | 21020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| DU1_Saf_Air_HEED | 21020093 | Air pressure too low | The air pressure is below the allowed operating level.
| DU1_Saf_Air_HEED | 21020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| DU1_DIface_Main | 21031000 | Discharge not ready | The corresponding distribution leg is not ready.
| DU1_DIface_Main | 21031001 | Ethernet communication fault | An ethernet fault with the packaging leg is active.
| DU1_DIface_Main | 21031002 | Disabled | The downstream interface is disabled.
| DU1_DIface_Main | 21031003 | Mc simulation discharge active | The simulation with the handshake signals row distributed and discharge belt empty is active.
| DU1_Ctr_Main | 21200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
| DU1_Ctr_Main | 21200002 | Distribution unit home needed | The distribution unit is stopping to home after restart.
| DU1_Ctr_Main | 21200004 | Remove all rows from diverter head or waiting belt | There are two possible actions: 1. After an Emergency stop or fault, all products have to be removed from the diverter head, or 2. with two row handling, all products have to be removed from the waiting belt. After removing the products, opening and closing the guard of the unit will automatically reset this message.
| DU1_Ctr_Main | 21200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| DU1_Ctr_Main | 21200006 | Distribution is switched off | The distribution unit is active, but the diverter remains at pass position and distributes all rows to the next distribution element.
| DU1_Ctr_Camera | 21200011 | Vision camera not ready | Vision camera is not ready.
| DU1_Ctr_Camera | 21200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| DU1_Ctr_Main | 21200014 | Too many rows in register | There are too many rows between the photoeye and the first move of the diverter.
| DU1_Ctr_Main | 21200015 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU1_Ctr_Main | 21200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU1_Ctr_Main | 21200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DU1_Ctr_Main | 21200020 | Diverter invalid position parameter | Diverter: The distance between the discharge- and the pass position is more than 180 degrees.
| DU1_Ctr_Main | 21200030 | Pusher rear position not valid | The rear position of well aligned rows is out of the pushers travel range.
| DU1_Ctr_Main | 21200031 | Pusher front position not valid | The front position is out of the pushers travel range.
| DU1_Ctr_Main | 21200040 | Pusher or waiting belt has not enough space to distribute a row | The parameter setting of the pusher or the waiting belt doesn`t allow to distribute a row with the set product length.
| DU1_AxDivr_Main | 21203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU1_AxDivr_Main | 21203001 | Position error | The controlled motor is out of the commanded position.
| DU1_AxDivr_Main | 21203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU1_AxDivr_Main | 21203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU1_AxDivr_Main | 21203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU1_AxDivr_Main | 21203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU1_AxDivr_Main | 21203023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU1_AxWaitBlt_Main | 21206000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU1_AxWaitBlt_Main | 21206001 | Position error | The controlled motor is out of the commanded position.
| DU1_AxWaitBlt_Main | 21206002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU1_AxWaitBlt_Main | 21206003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU1_AxWaitBlt_Main | 21206004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU1_AxWaitBlt_Main | 21206010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU1_WaitBltTrack_Main | 21207000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU1_WaitBltTrack_Main | 21207001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU1_WaitBltTrack_Main | 21207002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| DU1_WaitBltTrack_Main | 21207003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| DU1_WaitBltTrack_Main | 21207004 | Cylinder homing active | The cylinder is homing
| DU1_WaitBltTrack_Main | 21207005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| DU1_AxPush_Main | 21209000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU1_AxPush_Main | 21209001 | Position error | The controlled motor is out of the commanded position.
| DU1_AxPush_Main | 21209002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU1_AxPush_Main | 21209003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU1_AxPush_Main | 21209004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU1_AxPush_Main | 21209010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU1_AxPush_Main | 21209011 | Is not in the working area | The pusher ist not in the working area. Diverter and pusher moves are not possible.
| DU1_AxPush_Main | 21209023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU1_AxPushFlap_Main | 21210000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU1_AxPushFlap_Main | 21210001 | Position error | The controlled motor is out of the commanded position.
| DU1_AxPushFlap_Main | 21210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU1_AxPushFlap_Main | 21210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU1_AxPushFlap_Main | 21210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU1_AxPushFlap_Main | 21210007 | Brake released | Motor brake manually released.
| DU1_AxPushFlap_Main | 21210010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU1_AxPushFlap_Main | 21210023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU2_GMS_Main | 22004000 | Circuit breaker drive control voltage | The circuit breaker is switched off.
| DU2_GMS_Main | 22004001 | Circuit breaker belt tracking control voltage | The circuit breaker is switched off.
| DU2_GMS_Main | 22004002 | Converter fault | The converter is reporting a fault.
| DU2_SM_Main | 22010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DU2_SM_Main | 22010001 | Service mode active | The distribution unit is in service mode. No production active.
| DU2_SM_Main | 22010002 | Calculation active | The unit is in calculation state.
| DU2_SM_Main | 22010003 | Unit switched off | The unit is disabled.
| DU2_SM_Main | 22010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| DU2_SM_Main | 22010005 | Clean mode unit is active | The unit clean mode is active.
| DU2_SM_Main | 22010006 | Deactivated | The distribution unit is deactivated. No new rows will be distributed to the unit. Rows from within the unit will be discharged (the unit will be emptied).
| SFT_DU2_Saf | 22020010 | Door left 1 open | There is a guard on the machine which is open.
| SFT_DU2_Saf | 22020011 | Door left 2 open | There is a guard on the machine which is open.
| SFT_DU2_Saf | 22020012 | Door right 1 open | There is a guard on the machine which is open.
| SFT_DU2_Saf | 22020013 | Door right 2 open | There is a guard on the machine which is open.
| DU2_Saf_Cov | 22020018 | Doors open requested | The guard will be opened as soon as the last move is done.
| SFT_DU2_Saf | 22020060 | Energize drive fault Diverter | The energizing of the drive is faulted.
| SFT_DU2_Saf | 22020061 | Energize drive fault Waitbelt | The energizing of the drive is faulted.
| SFT_DU2_Saf | 22020062 | Energize drive fault Pusher | The energizing of the drive is faulted.
| SFT_DU2_Saf | 22020063 | Energize drive fault Pusher Flap | The energizing of the drive is faulted.
| SFT_DU2_Saf | 22020070 | Energize drive fault belt track Waitbelt | The energizing of the drive is faulted.
| DU2_Saf_Air_MS6SV | 22020090 | Exhaust valve fault | The exhaust valve has a fault.
| DU2_Saf_Air_MS6SV | 22020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_DU2_Saf | 22020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| DU2_Saf_Air_HEED | 22020093 | Air pressure too low | The air pressure is below the allowed operating level.
| DU2_Saf_Air_HEED | 22020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| DU2_DIface_Main | 22031000 | Discharge not ready or filling level of buffer not reached | The corresponding distribution leg is not ready or the filling level of the buffer to start the leg is not reached.
| DU2_DIface_Main | 22031001 | Ethernet communication fault | An ethernet fault with the packaging leg is active.
| DU2_DIface_Main | 22031002 | Disabled | The downstream interface is disabled.
| DU2_DIface_Main | 22031003 | Mc simulation active | The simulation with the handshake signals row distributed and discharge belt empty is active.
| DU2_Ctr_Main | 22200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
| DU2_Ctr_Main | 22200002 | Distribution unit home needed | The distribution unit is stopping to home after restart.
| DU2_Ctr_Main | 22200004 | Remove all rows from diverter head or waiting belt | There are two possible actions: 1. After an Emergency stop or fault, all products have to be removed from the diverter head, or 2. with two row handling, all products have to be removed from the waiting belt. After removing the products, opening and closing the guard of the unit will automatically reset this message.
| DU2_Ctr_Main | 22200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| DU2_Ctr_Main | 22200006 | Distribution is switched off | The distribution unit is active, but the diverter remains at pass position and distributes all rows to the next distribution element.
| DU2_Ctr_Camera | 22200011 | Vision camera not ready | Vision camera is not ready.
| DU2_Ctr_Camera | 22200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| DU2_Ctr_Main | 22200014 | Too many rows in register | There are too many rows between the photoeye and the first move of the diverter.
| DU2_Ctr_Main | 22200015 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU2_Ctr_Main | 22200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU2_Ctr_Main | 22200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DU2_Ctr_Main | 22200020 | Diverter invalid position parameter | The distance between the discharge position and the pass position is more than 180 degrees of the diverter.
| DU2_Ctr_Main | 22200030 | Pusher rear position not valid | The rear position of well aligned rows is out of the pushers travel range.
| DU2_Ctr_Main | 22200031 | Pusher front position not valid | The front position is out of the pushers travel range.
| DU2_Ctr_Main | 22200040 | Pusher or waiting belt has not enough space to distribute a row | The parameter setting of the pusher or the waiting belt doesn`t allow to distribute a row with the set product length.
| DU2_AxDivr_Main | 22203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU2_AxDivr_Main | 22203001 | Position error | The controlled motor is out of the commanded position.
| DU2_AxDivr_Main | 22203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU2_AxDivr_Main | 22203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU2_AxDivr_Main | 22203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU2_AxDivr_Main | 22203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU2_AxDivr_Main | 22203023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU2_AxWaitBlt_Main | 22206000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU2_AxWaitBlt_Main | 22206001 | Position error | The controlled motor is out of the commanded position.
| DU2_AxWaitBlt_Main | 22206002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU2_AxWaitBlt_Main | 22206003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU2_AxWaitBlt_Main | 22206004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU2_AxWaitBlt_Main | 22206010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU2_WaitBltTrack_Main | 22207000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU2_WaitBltTrack_Main | 22207001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU2_WaitBltTrack_Main | 22207002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| DU2_WaitBltTrack_Main | 22207003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| DU2_WaitBltTrack_Main | 22207004 | Cylinder homing active | The cylinder is homing
| DU2_WaitBltTrack_Main | 22207005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| DU2_AxPush_Main | 22209000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU2_AxPush_Main | 22209001 | Position error | The controlled motor is out of the commanded position.
| DU2_AxPush_Main | 22209002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU2_AxPush_Main | 22209003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU2_AxPush_Main | 22209004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU2_AxPush_Main | 22209010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU2_AxPush_Main | 22209011 | Is not in the working area | The pusher ist not in the working area. Diverter and pusher moves are not possible.
| DU2_AxPush_Main | 22209023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU2_AxPushFlap_Main | 22210000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU2_AxPushFlap_Main | 22210001 | Position error | The controlled motor is out of the commanded position.
| DU2_AxPushFlap_Main | 22210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU2_AxPushFlap_Main | 22210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU2_AxPushFlap_Main | 22210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU2_AxPushFlap_Main | 22210007 | Brake released | Motor brake manually released.
| DU2_AxPushFlap_Main | 22210010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU2_AxPushFlap_Main | 22210023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU3_GMS_Main | 23004000 | Circuit breaker drive control voltage | The circuit breaker is switched off.
| DU3_GMS_Main | 23004001 | Circuit breaker belt tracking control voltage | The circuit breaker is switched off.
| DU3_GMS_Main | 23004002 | Converter fault | The converter is reporting a fault.
| DU3_SM_Main | 23010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DU3_SM_Main | 23010001 | Service mode active | The distribution unit is in service mode. No production active.
| DU3_SM_Main | 23010002 | Calculation active | The unit is in calculation state.
| DU3_SM_Main | 23010003 | Unit switched off | The unit is disabled.
| DU3_SM_Main | 23010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| DU3_SM_Main | 23010005 | Clean mode unit is active | The unit clean mode is active.
| DU3_SM_Main | 23010006 | Deactivated | The distribution unit is deactivated. No new rows will be distributed to the unit. Rows from within the unit will be discharged (the unit will be emptied).
| SFT_DU3_Saf | 23020010 | Door left 1 open | There is a guard on the machine which is open.
| SFT_DU3_Saf | 23020011 | Door left 2 open | There is a guard on the machine which is open.
| SFT_DU3_Saf | 23020012 | Door right 1 open | There is a guard on the machine which is open.
| SFT_DU3_Saf | 23020013 | Door right 2 open | There is a guard on the machine which is open.
| DU3_Saf_Cov | 23020018 | Doors open requested | The guard will be opened as soon as the last move is done.
| SFT_DU3_Saf | 23020060 | Energize drive fault Diverter | The energizing of the drive is faulted.
| SFT_DU3_Saf | 23020061 | Energize drive fault Waitbelt | The energizing of the drive is faulted.
| SFT_DU3_Saf | 23020062 | Energize drive fault Pusher | The energizing of the drive is faulted.
| SFT_DU3_Saf | 23020063 | Energize drive fault Pusher Flap | The energizing of the drive is faulted.
| SFT_DU3_Saf | 23020070 | Energize drive fault belt track Waitbelt | The energizing of the drive is faulted.
| DU3_Saf_Air_MS6SV | 23020090 | Exhaust valve fault | The exhaust valve has a fault.
| DU3_Saf_Air_MS6SV | 23020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_DU3_Saf | 23020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| DU3_Saf_Air_HEED | 23020093 | Air pressure too low | The air pressure is below the allowed operating level.
| DU3_Saf_Air_HEED | 23020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| DU3_DIface_Main | 23031000 | Discharge not ready | The corresponding distribution leg is not ready.
| DU3_DIface_Main | 23031001 | Ethernet communication fault | An ethernet fault with the packaging leg is active.
| DU3_DIface_Main | 23031002 | Disabled | The downstream interface is disabled.
| DU3_DIface_Main | 23031003 | Mc simulation active | The simulation with the handshake signals row distributed and discharge belt empty is active.
| DU3_Ctr_Main | 23200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
| DU3_Ctr_Main | 23200002 | Distribution unit home needed | The distribution unit is stopping to home after restart.
| DU3_Ctr_Main | 23200004 | Remove all rows from diverter head or waiting belt | There are two possible actions: 1. After an Emergency stop or fault, all products have to be removed from the diverter head, or 2. with two row handling, all products have to be removed from the waiting belt. After removing the products, opening and closing the guard of the unit will automatically reset this message.
| DU3_Ctr_Main | 23200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| DU3_Ctr_Main | 23200006 | Distribution is switched off | The distribution unit is active, but the diverter remains at pass position and distributes all rows to the next distribution element.
| DU3_Ctr_Camera | 23200011 | Vision camera not ready | Vision camera is not ready.
| DU3_Ctr_Camera | 23200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| DU3_Ctr_Main | 23200014 | Too many rows in register | There are too many rows between the photoeye and the first move of the diverter.
| DU3_Ctr_Main | 23200015 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU3_Ctr_Main | 23200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU3_Ctr_Main | 23200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DU3_Ctr_Main | 23200020 | Diverter invalid position parameter | The distance between the discharge position and the pass position is more than 180 degrees of the diverter.
| DU3_Ctr_Main | 23200030 | Pusher rear position not valid | The rear position of well aligned rows is out of the pushers travel range.
| DU3_Ctr_Main | 23200031 | Pusher front position not valid | The front position is out of the pushers travel range.
| DU3_Ctr_Main | 23200040 | Pusher or waiting belt has not enough space to distribute a row | The parameter setting of the pusher or the waiting belt doesn`t allow to distribute a row with the set product length.
| DU3_AxDivr_Main | 23203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU3_AxDivr_Main | 23203001 | Position error | The controlled motor is out of the commanded position.
| DU3_AxDivr_Main | 23203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU3_AxDivr_Main | 23203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU3_AxDivr_Main | 23203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU3_AxDivr_Main | 23203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU3_AxDivr_Main | 23203023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU3_AxWaitBlt_Main | 23206000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU3_AxWaitBlt_Main | 23206001 | Position error | The controlled motor is out of the commanded position.
| DU3_AxWaitBlt_Main | 23206002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU3_AxWaitBlt_Main | 23206003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU3_AxWaitBlt_Main | 23206004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU3_AxWaitBlt_Main | 23206010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU3_WaitBltTrack_Main | 23207000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU3_WaitBltTrack_Main | 23207001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU3_WaitBltTrack_Main | 23207002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| DU3_WaitBltTrack_Main | 23207003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| DU3_WaitBltTrack_Main | 23207004 | Cylinder homing active | The cylinder is homing
| DU3_WaitBltTrack_Main | 23207005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| DU3_AxPush_Main | 23209000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU3_AxPush_Main | 23209001 | Position error | The controlled motor is out of the commanded position.
| DU3_AxPush_Main | 23209002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU3_AxPush_Main | 23209003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU3_AxPush_Main | 23209004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU3_AxPush_Main | 23209010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU3_AxPush_Main | 23209011 | Is not in the working area | The pusher ist not in the working area. Diverter and pusher moves are not possible.
| DU3_AxPush_Main | 23209023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU3_AxPushFlap_Main | 23210000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU3_AxPushFlap_Main | 23210001 | Position error | The controlled motor is out of the commanded position.
| DU3_AxPushFlap_Main | 23210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU3_AxPushFlap_Main | 23210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU3_AxPushFlap_Main | 23210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU3_AxPushFlap_Main | 23210007 | Brake released | Motor brake manually released.
| DU3_AxPushFlap_Main | 23210010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU3_AxPushFlap_Main | 23210023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU4_GMS_Main | 24004000 | Circuit breaker drive control voltage | The circuit breaker is switched off.
| DU4_GMS_Main | 24004001 | Circuit breaker belt tracking control voltage | The circuit breaker is switched off.
| DU4_GMS_Main | 24004002 | Converter fault | The converter is reporting a fault.
| DU4_SM_Main | 24010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DU4_SM_Main | 24010001 | Service mode active | The distribution unit is in service mode. No production active.
| DU4_SM_Main | 24010002 | Calculation active | The unit is in calculation state.
| DU4_SM_Main | 24010003 | Unit switched off | The unit is disabled.
| DU4_SM_Main | 24010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| DU4_SM_Main | 24010005 | Clean mode unit is active | The unit clean mode is active.
| DU4_SM_Main | 24010006 | Deactivated | The distribution unit is deactivated. No new rows will be distributed to the unit. Rows from within the unit will be discharged (the unit will be emptied).
| SFT_DU4_Saf | 24020010 | Door left 1 open | There is a guard on the machine which is open.
| SFT_DU4_Saf | 24020011 | Door left 2 open | There is a guard on the machine which is open.
| SFT_DU4_Saf | 24020012 | Door right 1 open | There is a guard on the machine which is open.
| SFT_DU4_Saf | 24020013 | Door right 2 open | There is a guard on the machine which is open.
| DU4_Saf_Cov | 24020018 | Doors open requested | The guard will be opened as soon as the last move is done.
| SFT_DU4_Saf | 24020060 | Energize drive fault Diverter | The energizing of the drive is faulted.
| SFT_DU4_Saf | 24020061 | Energize drive fault Waitbelt | The energizing of the drive is faulted.
| SFT_DU4_Saf | 24020062 | Energize drive fault Pusher | The energizing of the drive is faulted.
| SFT_DU4_Saf | 24020063 | Energize drive fault Pusher Flap | The energizing of the drive is faulted.
| SFT_DU4_Saf | 24020070 | Energize drive fault belt track Waitbelt | The energizing of the drive is faulted.
| DU4_Saf_Air_MS6SV | 24020090 | Exhaust valve fault | The exhaust valve has a fault.
| DU4_Saf_Air_MS6SV | 24020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_DU4_Saf | 24020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| DU4_Saf_Air_HEED | 24020093 | Air pressure too low | The air pressure is below the allowed operating level.
| DU4_Saf_Air_HEED | 24020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| DU4_DIface_Main | 24031000 | Discharge not ready | The corresponding distribution leg is not ready.
| DU4_DIface_Main | 24031001 | Ethernet communication fault | An ethernet fault with the packaging leg is active.
| DU4_DIface_Main | 24031002 | Disabled | The downstream interface is disabled.
| DU4_DIface_Main | 24031003 | Mc simulation active | The simulation with the handshake signals row distributed and discharge belt empty is active.
| DU4_Ctr_Main | 24200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
| DU4_Ctr_Main | 24200002 | Distribution unit home needed | The distribution unit is stopping to home after restart.
| DU4_Ctr_Main | 24200004 | Remove all rows from diverter head or waiting belt | There are two possible actions: 1. After an Emergency stop or fault, all products have to be removed from the diverter head, or 2. with two row handling, all products have to be removed from the waiting belt. After removing the products, opening and closing the guard of the unit will automatically reset this message.
| DU4_Ctr_Main | 24200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| DU4_Ctr_Main | 24200006 | Distribution is switched off | The distribution unit is active, but the diverter remains at pass position and distributes all rows to the next distribution element.
| DU4_Ctr_Camera | 24200011 | Vision camera not ready | Vision camera is not ready.
| DU4_Ctr_Camera | 24200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| DU4_Ctr_Main | 24200014 | Too many rows in register | There are too many rows between the photoeye and the first move of the diverter.
| DU4_Ctr_Main | 24200015 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU4_Ctr_Main | 24200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU4_Ctr_Main | 24200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DU4_Ctr_Main | 24200020 | Diverter invalid position parameter | The distance between the discharge position and the pass position is more than 180 degrees of the diverter.
| DU4_Ctr_Main | 24200030 | Pusher rear position not valid | The rear position of well aligned rows is out of the pushers travel range.
| DU4_Ctr_Main | 24200031 | Pusher front position not valid | The front position is out of the pushers travel range.
| DU4_Ctr_Main | 24200040 | Pusher or waiting belt has not enough space to distribute a row | The parameter setting of the pusher or the waiting belt doesn`t allow to distribute a row with the set product length.
| DU4_AxDivr_Main | 24203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU4_AxDivr_Main | 24203001 | Position error | The controlled motor is out of the commanded position.
| DU4_AxDivr_Main | 24203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU4_AxDivr_Main | 24203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU4_AxDivr_Main | 24203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU4_AxDivr_Main | 24203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU4_AxDivr_Main | 24203023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU4_AxWaitBlt_Main | 24206000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU4_AxWaitBlt_Main | 24206001 | Position error | The controlled motor is out of the commanded position.
| DU4_AxWaitBlt_Main | 24206002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU4_AxWaitBlt_Main | 24206003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU4_AxWaitBlt_Main | 24206004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU4_AxWaitBlt_Main | 24206010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU4_WaitBltTrack_Main | 24207000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU4_WaitBltTrack_Main | 24207001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU4_WaitBltTrack_Main | 24207002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| DU4_WaitBltTrack_Main | 24207003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| DU4_WaitBltTrack_Main | 24207004 | Cylinder homing active | The cylinder is homing
| DU4_WaitBltTrack_Main | 24207005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| DU4_AxPush_Main | 24209000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU4_AxPush_Main | 24209001 | Position error | The controlled motor is out of the commanded position.
| DU4_AxPush_Main | 24209002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU4_AxPush_Main | 24209003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU4_AxPush_Main | 24209004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU4_AxPush_Main | 24209010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU4_AxPush_Main | 24209011 | Is not in the working area | The pusher ist not in the working area. Diverter and pusher moves are not possible.
| DU4_AxPush_Main | 24209023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU4_AxPushFlap_Main | 24210000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU4_AxPushFlap_Main | 24210001 | Position error | The controlled motor is out of the commanded position.
| DU4_AxPushFlap_Main | 24210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU4_AxPushFlap_Main | 24210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU4_AxPushFlap_Main | 24210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU4_AxPushFlap_Main | 24210007 | Brake released | Motor brake manually released.
| DU4_AxPushFlap_Main | 24210010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU4_AxPushFlap_Main | 24210023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU5_GMS_Main | 25004000 | Circuit breaker drive control voltage | The circuit breaker is switched off.
| DU5_GMS_Main | 25004001 | Circuit breaker belt tracking control voltage | The circuit breaker is switched off.
| DU5_GMS_Main | 25004002 | Converter fault | The converter is reporting a fault.
| DU5_SM_Main | 25010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DU5_SM_Main | 25010001 | Service mode active | The distribution unit is in service mode. No production active.
| DU5_SM_Main | 25010002 | Calculation active | The unit is in calculation state.
| DU5_SM_Main | 25010003 | Unit switched off | The unit is disabled.
| DU5_SM_Main | 25010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| DU5_SM_Main | 25010005 | Clean mode unit is active | The unit clean mode is active.
| DU5_SM_Main | 25010006 | Deactivated | The distribution unit is deactivated. No new rows will be distributed to the unit. Rows from within the unit will be discharged (the unit will be emptied).
| SFT_DU5_Saf | 25020010 | Door left 1 open | There is a guard on the machine which is open.
| SFT_DU5_Saf | 25020011 | Door left 2 open | There is a guard on the machine which is open.
| SFT_DU5_Saf | 25020012 | Door right 1 open | There is a guard on the machine which is open.
| SFT_DU5_Saf | 25020013 | Door right 2 open | There is a guard on the machine which is open.
| DU5_Saf_Cov | 25020018 | Doors open requested | The guard will be opened as soon as the last move is done.
| SFT_DU5_Saf | 25020060 | Energize drive fault Diverter | The energizing of the drive is faulted.
| SFT_DU5_Saf | 25020061 | Energize drive fault Waitbelt | The energizing of the drive is faulted.
| SFT_DU5_Saf | 25020062 | Energize drive fault Pusher | The energizing of the drive is faulted.
| SFT_DU5_Saf | 25020063 | Energize drive fault Pusher Flap | The energizing of the drive is faulted.
| SFT_DU5_Saf | 25020070 | Energize drive fault belt track Waitbelt | The energizing of the drive is faulted.
| DU5_Saf_Air_MS6SV | 25020090 | Exhaust valve fault | The exhaust valve has a fault.
| DU5_Saf_Air_MS6SV | 25020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_DU5_Saf | 25020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| DU5_Saf_Air_HEED | 25020093 | Air pressure too low | The air pressure is below the allowed operating level.
| DU5_Saf_Air_HEED | 25020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| DU5_DIface_Main | 25031000 | Discharge not ready | The corresponding distribution leg is not ready.
| DU5_DIface_Main | 25031001 | Ethernet communication fault | An ethernet fault with the packaging leg is active.
| DU5_DIface_Main | 25031002 | Disabled | The downstream interface is disabled.
| DU5_DIface_Main | 25031003 | Mc simulation active | The simulation with the handshake signals row distributed and discharge belt empty is active.
| DU5_Ctr_Main | 25200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
| DU5_Ctr_Main | 25200002 | Distribution unit home needed | The distribution unit is stopping to home after restart.
| DU5_Ctr_Main | 25200004 | Remove all rows from diverter head or waiting belt | There are two possible actions: 1. After an Emergency stop or fault, all products have to be removed from the diverter head, or 2. with two row handling, all products have to be removed from the waiting belt. After removing the products, opening and closing the guard of the unit will automatically reset this message.
| DU5_Ctr_Main | 25200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| DU5_Ctr_Main | 25200006 | Distribution is switched off | The distribution unit is active, but the diverter remains at pass position and distributes all rows to the next distribution element.
| DU5_Ctr_Camera | 25200011 | Vision camera not ready | Vision camera is not ready.
| DU5_Ctr_Camera | 25200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| DU5_Ctr_Main | 25200014 | Too many rows in register | There are too many rows between the photoeye and the first move of the diverter.
| DU5_Ctr_Main | 25200015 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU5_Ctr_Main | 25200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DU5_Ctr_Main | 25200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DU5_Ctr_Main | 25200020 | Diverter invalid position parameter | The distance between the discharge position and the pass position is more than 180 degrees of the diverter.
| DU5_Ctr_Main | 25200030 | Pusher rear position not valid | The rear position of well aligned rows is out of the pushers travel range.
| DU5_Ctr_Main | 25200031 | Pusher front position not valid | The front position is out of the pushers travel range.
| DU5_Ctr_Main | 25200040 | Pusher or waiting belt has not enough space to distribute a row | The parameter setting of the pusher or the waiting belt doesn`t allow to distribute a row with the set product length.
| DU5_AxDivr_Main | 25203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU5_AxDivr_Main | 25203001 | Position error | The controlled motor is out of the commanded position.
| DU5_AxDivr_Main | 25203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU5_AxDivr_Main | 25203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU5_AxDivr_Main | 25203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU5_AxDivr_Main | 25203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU5_AxDivr_Main | 25203023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU5_AxWaitBlt_Main | 25206000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU5_AxWaitBlt_Main | 25206001 | Position error | The controlled motor is out of the commanded position.
| DU5_AxWaitBlt_Main | 25206002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU5_AxWaitBlt_Main | 25206003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU5_AxWaitBlt_Main | 25206004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU5_AxWaitBlt_Main | 25206010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU5_WaitBltTrack_Main | 25207000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU5_WaitBltTrack_Main | 25207001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DU5_WaitBltTrack_Main | 25207002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| DU5_WaitBltTrack_Main | 25207003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| DU5_WaitBltTrack_Main | 25207004 | Cylinder homing active | The cylinder is homing
| DU5_WaitBltTrack_Main | 25207005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| DU5_AxPush_Main | 25209000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU5_AxPush_Main | 25209001 | Position error | The controlled motor is out of the commanded position.
| DU5_AxPush_Main | 25209002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU5_AxPush_Main | 25209003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU5_AxPush_Main | 25209004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU5_AxPush_Main | 25209010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU5_AxPush_Main | 25209011 | Is not in the working area | The pusher ist not in the working area. Diverter and pusher moves are not possible.
| DU5_AxPush_Main | 25209023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DU5_AxPushFlap_Main | 25210000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DU5_AxPushFlap_Main | 25210001 | Position error | The controlled motor is out of the commanded position.
| DU5_AxPushFlap_Main | 25210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DU5_AxPushFlap_Main | 25210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DU5_AxPushFlap_Main | 25210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DU5_AxPushFlap_Main | 25210007 | Brake released | Motor brake manually released.
| DU5_AxPushFlap_Main | 25210010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DU5_AxPushFlap_Main | 25210023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DUR_GMS_Main | 30004000 | Circuit breaker drive control voltage | The circuit breaker is switched off.
| DUR_GMS_Main | 30004001 | Circuit breaker belt tracking control voltage | The circuit breaker is switched off.
| DUR_GMS_Main | 30004002 | Converter fault | The converter is reporting a fault.
| DUR_SM_Main | 30010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DUR_SM_Main | 30010001 | Service mode active | The distribution unit is in service mode. No production active.
| DUR_SM_Main | 30010002 | Calculation active | The unit is in calculation state.
| DUR_SM_Main | 30010003 | Unit switched off | The unit is disabled.
| DUR_SM_Main | 30010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| DUR_SM_Main | 30010005 | Clean mode unit is active | The unit clean mode is active.
| DUR_SM_Main | 30010006 | Deactivated | The distribution unit is deactivated. No new rows will be distributed to the unit. Rows from within the unit will be discharged (the unit will be emptied).
| SFT_DUR_Saf | 30020010 | Door left 1 open | There is a guard on the machine which is open.
| SFT_DUR_Saf | 30020011 | Door left 2 open | There is a guard on the machine which is open.
| SFT_DUR_Saf | 30020012 | Door right 1 open | There is a guard on the machine which is open.
| SFT_DUR_Saf | 30020013 | Door right 2 open | There is a guard on the machine which is open.
| SFT_DUR_Saf | 30020014 | Discharge belt not in working position | The discharge belt is not in working position
| DUR_Saf_Cov | 30020018 | Doors open requested | The guard will be opened as soon as the last move is done.
| SFT_DUR_Saf | 30020060 | Energize drive fault Diverter | The energizing of the drive is faulted.
| SFT_DUR_Saf | 30020061 | Energize drive fault Waitbelt | The energizing of the drive is faulted.
| SFT_DUR_Saf | 30020062 | Energize drive fault Pusher | The energizing of the drive is faulted.
| SFT_DUR_Saf | 30020063 | Energize drive fault Pusher Flap | The energizing of the drive is faulted.
| SFT_DUR_Saf | 30020070 | Energize drive fault belt track Waitbelt | The energizing of the drive is faulted.
| DUR_Saf_Air_MS6SV | 30020090 | Exhaust valve fault | The exhaust valve has a fault.
| DUR_Saf_Air_MS6SV | 30020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_DUR_Saf | 30020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| DUR_Saf_Air_HEED | 30020093 | Air pressure too low | The air pressure is below the allowed operating level.
| DUR_Saf_Air_HEED | 30020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| DUR_DIface_Main | 30031000 | Discharge not ready | The corresponding distribution leg is not ready.
| DUR_DIface_Main | 30031001 | Ethernet communication fault | An ethernet fault with the packaging leg is active.
| DUR_DIface_Main | 30031002 | Disabled | The downstream interface is disabled.
| DUR_DIface_Main | 30031003 | Mc simulation active | The simulation with the handshake signals row distributed and discharge belt empty is active.
| DUR_Ctr_Main | 30200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
| DUR_Ctr_Main | 30200002 | Distribution unit home needed | The distribution unit is stopping to home after restart.
| DUR_Ctr_Main | 30200004 | Remove all rows from diverter head or waiting belt | There are two possible actions: 1. After an Emergency stop or fault, all products have to be removed from the diverter head, or 2. with two row handling, all products have to be removed from the waiting belt. After removing the products, opening and closing the guard of the unit will automatically reset this message.
| DUR_Ctr_Main | 30200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| DUR_Ctr_Main | 30200006 | Distribution is switched off | The distribution unit is active, but the diverter remains at pass position and distributes all rows to the next distribution element.
| DUR_Ctr_Main | 30200007 | Recycling inhibited due to belt tracking | The belt edge of the DUR belt is not near the middle. To help the belt edge to come back to the middle, recycling is inhibited.
| DUR_Ctr_Camera | 30200011 | Vision camera not ready | Vision camera is not ready.
| DUR_Ctr_Camera | 30200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| DUR_Ctr_Main | 30200014 | Too many rows in register | There are too many rows between the photoeye and the first move of the diverter.
| DUR_Ctr_Main | 30200015 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DUR_Ctr_Main | 30200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DUR_Ctr_Main | 30200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DUR_Ctr_Main | 30200020 | Diverter invalid position parameter | The distance between the discharge position and the pass position is more than 180 degrees of the diverter.
| DUR_Ctr_Main | 30200030 | Pusher rear position not valid | The rear position of well aligned rows is out of the pushers travel range.
| DUR_Ctr_Main | 30200031 | Pusher front position not valid | The front position is out of the pushers travel range.
| DUR_Ctr_Main | 30200040 | Pusher or waiting belt has not enough space to distribute a row | The parameter setting of the pusher or the waiting belt doesn`t allow to distribute a row with the set product length.
| DUR_AxDivr_Main | 30203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DUR_AxDivr_Main | 30203001 | Position error | The controlled motor is out of the commanded position.
| DUR_AxDivr_Main | 30203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DUR_AxDivr_Main | 30203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DUR_AxDivr_Main | 30203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DUR_AxDivr_Main | 30203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DUR_AxDivr_Main | 30203023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DUR_AxWaitBlt_Main | 30206000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DUR_AxWaitBlt_Main | 30206001 | Position error | The controlled motor is out of the commanded position.
| DUR_AxWaitBlt_Main | 30206002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DUR_AxWaitBlt_Main | 30206003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DUR_AxWaitBlt_Main | 30206004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DUR_AxWaitBlt_Main | 30206010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DUR_WaitBltTrack_Main | 30207000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DUR_WaitBltTrack_Main | 30207001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
| DUR_WaitBltTrack_Main | 30207002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
| DUR_WaitBltTrack_Main | 30207003 | Cylinder fault | This fault can have several causes. 1 .The cylinder is not connected or wrong mounted. 2. The cylinder is mechanically blocked or defective.
| DUR_WaitBltTrack_Main | 30207004 | Cylinder homing active | The cylinder is homing
| DUR_WaitBltTrack_Main | 30207005 | Cylinder too long active | The cylinder was active for a too long time or it has to do too much correction cycles
| DUR_AxPush_Main | 30209000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DUR_AxPush_Main | 30209001 | Position error | The controlled motor is out of the commanded position.
| DUR_AxPush_Main | 30209002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DUR_AxPush_Main | 30209003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DUR_AxPush_Main | 30209004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DUR_AxPush_Main | 30209010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DUR_AxPush_Main | 30209011 | Is not in the working area | The pusher ist not in the working area. Diverter and pusher moves are not possible.
| DUR_AxPush_Main | 30209023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DUR_AxPushFlap_Main | 30210000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DUR_AxPushFlap_Main | 30210001 | Position error | The controlled motor is out of the commanded position.
| DUR_AxPushFlap_Main | 30210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DUR_AxPushFlap_Main | 30210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DUR_AxPushFlap_Main | 30210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DUR_AxPushFlap_Main | 30210007 | Brake released | Motor brake manually released.
| DUR_AxPushFlap_Main | 30210010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DUR_AxPushFlap_Main | 30210023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| GAPCLO1_SM_Main | 31010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO1_SM_Main | 31010002 | Calculation active | The unit is in calculation state.
| GAPCLO1_SM_Main | 31010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO1_SM_Main | 31010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLO1_Saf_Main | 31020060 | Energize drive fault Discharge belt | The energizing of the drive is faulted.
| SFT_GAPCLO1_Saf_Main | 31020061 | Energize drive fault belt 1 | The energizing of the drive is faulted.
| SFT_GAPCLO1_Saf_Main | 31020062 | Energize drive fault belt 2 | The energizing of the drive is faulted.
| SFT_GAPCLO1_Saf_Main | 31020063 | Energize drive fault FXX1 Transport belt 1 | The energizing of the drive is faulted.
| FXX1_AxTranspBlt1_Main | 31201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX1_AxTranspBlt1_Main | 31201001 | Position error | The controlled motor is out of the commanded position.
| FXX1_AxTranspBlt1_Main | 31201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX1_AxTranspBlt1_Main | 31201003 | Validation fault | The module detected a value out of range.
| FXX1_AxTranspBlt1_Main | 31201004 | Switched off | The motor has been switched off temporarily.
| FXX1_AxTranspBlt2_Main | 31202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX1_AxTranspBlt2_Main | 31202001 | Position error | The controlled motor is out of the commanded position.
| FXX1_AxTranspBlt2_Main | 31202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX1_AxTranspBlt2_Main | 31202003 | Validation fault | The module detected a value out of range.
| FXX1_AxTranspBlt2_Main | 31202004 | Switched off | The motor has been switched off temporarily.
| FXX1_AxTranspBlt3_Main | 31203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX1_AxTranspBlt3_Main | 31203001 | Position error | The controlled motor is out of the commanded position.
| FXX1_AxTranspBlt3_Main | 31203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX1_AxTranspBlt3_Main | 31203003 | Validation fault | The module detected a value out of range.
| FXX1_AxTranspBlt3_Main | 31203004 | Switched off | The motor has been switched off temporarily.
| GAPCLO1_Ctr_Main | 31300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLO1_Ctr_Main | 31300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLO1_Ctr_Main | 31300002 | Homing active | The feeding system is homing or synchronising
| GAPCLO1_AxDischBlt_Main | 31301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO1_AxDischBlt_Main | 31301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO1_AxDischBlt_Main | 31301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO1_AxDischBlt_Main | 31301003 | Validation fault | The module detected a value out of range.
| GAPCLO1_AxDischBlt_Main | 31301004 | Switched off | The motor has been switched off temporarily.
| GAPCLO1_AxBlt1_Main | 31302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO1_AxBlt1_Main | 31302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO1_AxBlt1_Main | 31302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO1_AxBlt1_Main | 31302003 | Validation fault | The module detected a value out of range.
| GAPCLO1_AxBlt1_Main | 31302004 | Switched off | The motor has been switched off temporarily.
| GAPCLO1_AxBlt2_Main | 31303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO1_AxBlt2_Main | 31303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO1_AxBlt2_Main | 31303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO1_AxBlt2_Main | 31303003 | Validation fault | The module detected a value out of range.
| GAPCLO1_AxBlt2_Main | 31303004 | Switched off | The motor has been switched off temporarily.
| GAPCLO1_AxDischBltUp_Main | 31321000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO1_AxDischBltUp_Main | 31321001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO1_AxDischBltUp_Main | 31321002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO1_AxDischBltUp_Main | 31321003 | Validation fault | The module detected a value out of range.
| GAPCLO1_AxDischBltUp_Main | 31321004 | Switched off | The motor has been switched off temporarily.
| GAPCLO1_AxDischBltLow_Main | 31322000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO1_AxDischBltLow_Main | 31322001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO1_AxDischBltLow_Main | 31322002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO1_AxDischBltLow_Main | 31322003 | Validation fault | The module detected a value out of range.
| GAPCLO1_AxDischBltLow_Main | 31322004 | Switched off | The motor has been switched off temporarily.
| GAPCLO1_AxDivr_Main | 31330000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO1_AxDivr_Main | 31330001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO1_AxDivr_Main | 31330002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO1_AxDivr_Main | 31330003 | Validation fault | The module detected a value out of range.
| GAPCLO1_AxDivr_Main | 31330004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| GAPCLO1_AxDivr_Main | 31330006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
| GAPCLO1_AxDivr_Main | 31330010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| GAPCLO1_AxDivr_Main | 31330020 | Invalid position parameter | The distance between up and down position is more than 180 degrees.
| GAPCLO2_SM_Main | 32010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO2_SM_Main | 32010002 | Calculation active | The unit is in calculation state.
| GAPCLO2_SM_Main | 32010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO2_SM_Main | 32010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLO2_Saf_Main | 32020060 | Energize drive fault Discharge belt | The energizing of the drive is faulted.
| SFT_GAPCLO2_Saf_Main | 32020061 | Energize drive fault belt 1 | The energizing of the drive is faulted.
| SFT_GAPCLO2_Saf_Main | 32020062 | Energize drive fault belt 2 | The energizing of the drive is faulted.
| FXX2_AxTranspBlt1_Main | 32201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX2_AxTranspBlt1_Main | 32201001 | Position error | The controlled motor is out of the commanded position.
| FXX2_AxTranspBlt1_Main | 32201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX2_AxTranspBlt1_Main | 32201003 | Validation fault | The module detected a value out of range.
| FXX2_AxTranspBlt1_Main | 32201004 | Switched off | The motor has been switched off temporarily.
| FXX2_AxTranspBlt2_Main | 32202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX2_AxTranspBlt2_Main | 32202001 | Position error | The controlled motor is out of the commanded position.
| FXX2_AxTranspBlt2_Main | 32202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX2_AxTranspBlt2_Main | 32202003 | Validation fault | The module detected a value out of range.
| FXX2_AxTranspBlt2_Main | 32202004 | Switched off | The motor has been switched off temporarily.
| FXX2_AxTranspBlt3_Main | 32203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX2_AxTranspBlt3_Main | 32203001 | Position error | The controlled motor is out of the commanded position.
| FXX2_AxTranspBlt3_Main | 32203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX2_AxTranspBlt3_Main | 32203003 | Validation fault | The module detected a value out of range.
| FXX2_AxTranspBlt3_Main | 32203004 | Switched off | The motor has been switched off temporarily.
| GAPCLO2_Ctr_Main | 32300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLO2_Ctr_Main | 32300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLO2_Ctr_Main | 32300002 | Homing active | The feeding system is homing or synchronising
| GAPCLO2_AxDischBlt_Main | 32301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO2_AxDischBlt_Main | 32301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO2_AxDischBlt_Main | 32301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO2_AxDischBlt_Main | 32301003 | Validation fault | The module detected a value out of range.
| GAPCLO2_AxDischBlt_Main | 32301004 | Switched off | The motor has been switched off temporarily.
| GAPCLO2_AxBlt1_Main | 32302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO2_AxBlt1_Main | 32302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO2_AxBlt1_Main | 32302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO2_AxBlt1_Main | 32302003 | Validation fault | The module detected a value out of range.
| GAPCLO2_AxBlt1_Main | 32302004 | Switched off | The motor has been switched off temporarily.
| GAPCLO2_AxBlt2_Main | 32303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO2_AxBlt2_Main | 32303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO2_AxBlt2_Main | 32303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO2_AxBlt2_Main | 32303003 | Validation fault | The module detected a value out of range.
| GAPCLO2_AxBlt2_Main | 32303004 | Switched off | The motor has been switched off temporarily.
| GAPCLO2_AxDischBltUp_Main | 32321000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO2_AxDischBltUp_Main | 32321001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO2_AxDischBltUp_Main | 32321002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO2_AxDischBltUp_Main | 32321003 | Validation fault | The module detected a value out of range.
| GAPCLO2_AxDischBltUp_Main | 32321004 | Switched off | The motor has been switched off temporarily.
| GAPCLO2_AxDischBltLow_Main | 32322000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO2_AxDischBltLow_Main | 32322001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO2_AxDischBltLow_Main | 32322002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO2_AxDischBltLow_Main | 32322003 | Validation fault | The module detected a value out of range.
| GAPCLO2_AxDischBltLow_Main | 32322004 | Switched off | The motor has been switched off temporarily.
| GAPCLO2_AxDivr_Main | 32330000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO2_AxDivr_Main | 32330001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO2_AxDivr_Main | 32330002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO2_AxDivr_Main | 32330003 | Validation fault | The module detected a value out of range.
| GAPCLO2_AxDivr_Main | 32330004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| GAPCLO2_AxDivr_Main | 32330006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
| GAPCLO2_AxDivr_Main | 32330010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| GAPCLO2_AxDivr_Main | 32330020 | Invalid position parameter | The distance between up and down position is more than 180 degrees.
| GAPCLO3_SM_Main | 33010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO3_SM_Main | 33010002 | Calculation active | The unit is in calculation state.
| GAPCLO3_SM_Main | 33010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO3_SM_Main | 33010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLO3_Saf_Main | 33020060 | Energize drives fault | The energizing of the drive is faulted.
| FXX3_AxTranspBlt1_Main | 33201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX3_AxTranspBlt1_Main | 33201001 | Position error | The controlled motor is out of the commanded position.
| FXX3_AxTranspBlt1_Main | 33201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX3_AxTranspBlt1_Main | 33201003 | Validation fault | The module detected a value out of range.
| FXX3_AxTranspBlt1_Main | 33201004 | Switched off | The motor has been switched off temporarily.
| FXX3_AxTranspBlt2_Main | 33202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX3_AxTranspBlt2_Main | 33202001 | Position error | The controlled motor is out of the commanded position.
| FXX3_AxTranspBlt2_Main | 33202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX3_AxTranspBlt2_Main | 33202003 | Validation fault | The module detected a value out of range.
| FXX3_AxTranspBlt2_Main | 33202004 | Switched off | The motor has been switched off temporarily.
| FXX3_AxTranspBlt3_Main | 33203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX3_AxTranspBlt3_Main | 33203001 | Position error | The controlled motor is out of the commanded position.
| FXX3_AxTranspBlt3_Main | 33203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX3_AxTranspBlt3_Main | 33203003 | Validation fault | The module detected a value out of range.
| FXX3_AxTranspBlt3_Main | 33203004 | Switched off | The motor has been switched off temporarily.
| GAPCLO3_Ctr_Main | 33300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLO3_Ctr_Main | 33300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLO3_Ctr_Main | 33300002 | Homing active | The feeding system is homing or synchronising
| GAPCLO3_AxDischBlt_Main | 33301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO3_AxDischBlt_Main | 33301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO3_AxDischBlt_Main | 33301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO3_AxDischBlt_Main | 33301003 | Validation fault | The module detected a value out of range.
| GAPCLO3_AxDischBlt_Main | 33301004 | Switched off | The motor has been switched off temporarily.
| GAPCLO3_AxBlt1_Main | 33302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO3_AxBlt1_Main | 33302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO3_AxBlt1_Main | 33302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO3_AxBlt1_Main | 33302003 | Validation fault | The module detected a value out of range.
| GAPCLO3_AxBlt1_Main | 33302004 | Switched off | The motor has been switched off temporarily.
| GAPCLO3_AxBlt2_Main | 33303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO3_AxBlt2_Main | 33303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO3_AxBlt2_Main | 33303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO3_AxBlt2_Main | 33303003 | Validation fault | The module detected a value out of range.
| GAPCLO3_AxBlt2_Main | 33303004 | Switched off | The motor has been switched off temporarily.
| GAPCLO4_SM_Main | 34010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO4_SM_Main | 34010002 | Calculation active | The unit is in calculation state.
| GAPCLO4_SM_Main | 34010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO4_SM_Main | 34010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLO4_Saf_Main | 34020060 | Energize drives fault | The energizing of the drive is faulted.
| FXX4_AxTranspBlt1_Main | 34201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX4_AxTranspBlt1_Main | 34201001 | Position error | The controlled motor is out of the commanded position.
| FXX4_AxTranspBlt1_Main | 34201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX4_AxTranspBlt1_Main | 34201003 | Validation fault | The module detected a value out of range.
| FXX4_AxTranspBlt1_Main | 34201004 | Switched off | The motor has been switched off temporarily.
| FXX4_AxTranspBlt2_Main | 34202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX4_AxTranspBlt2_Main | 34202001 | Position error | The controlled motor is out of the commanded position.
| FXX4_AxTranspBlt2_Main | 34202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX4_AxTranspBlt2_Main | 34202003 | Validation fault | The module detected a value out of range.
| FXX4_AxTranspBlt2_Main | 34202004 | Switched off | The motor has been switched off temporarily.
| FXX4_AxTranspBlt3_Main | 34203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX4_AxTranspBlt3_Main | 34203001 | Position error | The controlled motor is out of the commanded position.
| FXX4_AxTranspBlt3_Main | 34203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX4_AxTranspBlt3_Main | 34203003 | Validation fault | The module detected a value out of range.
| FXX4_AxTranspBlt3_Main | 34203004 | Switched off | The motor has been switched off temporarily.
| GAPCLO4_Ctr_Main | 34300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLO4_Ctr_Main | 34300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLO4_Ctr_Main | 34300002 | Homing active | The feeding system is homing or synchronising
| GAPCLO4_AxDischBlt_Main | 34301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO4_AxDischBlt_Main | 34301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO4_AxDischBlt_Main | 34301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO4_AxDischBlt_Main | 34301003 | Validation fault | The module detected a value out of range.
| GAPCLO4_AxDischBlt_Main | 34301004 | Switched off | The motor has been switched off temporarily.
| GAPCLO4_AxBlt1_Main | 34302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO4_AxBlt1_Main | 34302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO4_AxBlt1_Main | 34302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO4_AxBlt1_Main | 34302003 | Validation fault | The module detected a value out of range.
| GAPCLO4_AxBlt1_Main | 34302004 | Switched off | The motor has been switched off temporarily.
| GAPCLO4_AxBlt2_Main | 34303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO4_AxBlt2_Main | 34303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO4_AxBlt2_Main | 34303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO4_AxBlt2_Main | 34303003 | Validation fault | The module detected a value out of range.
| GAPCLO4_AxBlt2_Main | 34303004 | Switched off | The motor has been switched off temporarily.
| GAPCLO5_SM_Main | 35010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO5_SM_Main | 35010002 | Calculation active | The unit is in calculation state.
| GAPCLO5_SM_Main | 35010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO5_SM_Main | 35010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLO5_Saf_Main | 35020060 | Energize drives fault | The energizing of the drive is faulted.
| FXX5_AxTranspBlt1_Main | 35201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX5_AxTranspBlt1_Main | 35201001 | Position error | The controlled motor is out of the commanded position.
| FXX5_AxTranspBlt1_Main | 35201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX5_AxTranspBlt1_Main | 35201003 | Validation fault | The module detected a value out of range.
| FXX5_AxTranspBlt1_Main | 35201004 | Switched off | The motor has been switched off temporarily.
| FXX5_AxTranspBlt2_Main | 35202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX5_AxTranspBlt2_Main | 35202001 | Position error | The controlled motor is out of the commanded position.
| FXX5_AxTranspBlt2_Main | 35202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX5_AxTranspBlt2_Main | 35202003 | Validation fault | The module detected a value out of range.
| FXX5_AxTranspBlt2_Main | 35202004 | Switched off | The motor has been switched off temporarily.
| FXX5_AxTranspBlt3_Main | 35203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX5_AxTranspBlt3_Main | 35203001 | Position error | The controlled motor is out of the commanded position.
| FXX5_AxTranspBlt3_Main | 35203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX5_AxTranspBlt3_Main | 35203003 | Validation fault | The module detected a value out of range.
| FXX5_AxTranspBlt3_Main | 35203004 | Switched off | The motor has been switched off temporarily.
| GAPCLO5_Ctr_Main | 35300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLO5_Ctr_Main | 35300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLO5_Ctr_Main | 35300002 | Homing active | The feeding system is homing or synchronising
| GAPCLO5_AxDischBlt_Main | 35301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO5_AxDischBlt_Main | 35301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO5_AxDischBlt_Main | 35301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO5_AxDischBlt_Main | 35301003 | Validation fault | The module detected a value out of range.
| GAPCLO5_AxDischBlt_Main | 35301004 | Switched off | The motor has been switched off temporarily.
| GAPCLO5_AxBlt1_Main | 35302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO5_AxBlt1_Main | 35302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO5_AxBlt1_Main | 35302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO5_AxBlt1_Main | 35302003 | Validation fault | The module detected a value out of range.
| GAPCLO5_AxBlt1_Main | 35302004 | Switched off | The motor has been switched off temporarily.
| GAPCLO5_AxBlt2_Main | 35303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO5_AxBlt2_Main | 35303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO5_AxBlt2_Main | 35303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO5_AxBlt2_Main | 35303003 | Validation fault | The module detected a value out of range.
| GAPCLO5_AxBlt2_Main | 35303004 | Switched off | The motor has been switched off temporarily.
| GAPCLO6_SM_Main | 36010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO6_SM_Main | 36010002 | Calculation active | The unit is in calculation state.
| GAPCLO6_SM_Main | 36010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO6_SM_Main | 36010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLO6_Saf_Main | 36020060 | Energize drives fault | The energizing of the drive is faulted.
| FXX6_AxTranspBlt1_Main | 36201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX6_AxTranspBlt1_Main | 36201001 | Position error | The controlled motor is out of the commanded position.
| FXX6_AxTranspBlt1_Main | 36201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX6_AxTranspBlt1_Main | 36201003 | Validation fault | The module detected a value out of range.
| FXX6_AxTranspBlt1_Main | 36201004 | Switched off | The motor has been switched off temporarily.
| FXX6_AxTranspBlt2_Main | 36202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX6_AxTranspBlt2_Main | 36202001 | Position error | The controlled motor is out of the commanded position.
| FXX6_AxTranspBlt2_Main | 36202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX6_AxTranspBlt2_Main | 36202003 | Validation fault | The module detected a value out of range.
| FXX6_AxTranspBlt2_Main | 36202004 | Switched off | The motor has been switched off temporarily.
| FXX6_AxTranspBlt3_Main | 36203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX6_AxTranspBlt3_Main | 36203001 | Position error | The controlled motor is out of the commanded position.
| FXX6_AxTranspBlt3_Main | 36203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX6_AxTranspBlt3_Main | 36203003 | Validation fault | The module detected a value out of range.
| FXX6_AxTranspBlt3_Main | 36203004 | Switched off | The motor has been switched off temporarily.
| GAPCLO6_Ctr_Main | 36300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLO6_Ctr_Main | 36300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLO6_Ctr_Main | 36300002 | Homing active | The feeding system is homing or synchronising
| GAPCLO6_AxDischBlt_Main | 36301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO6_AxDischBlt_Main | 36301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO6_AxDischBlt_Main | 36301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO6_AxDischBlt_Main | 36301003 | Validation fault | The module detected a value out of range.
| GAPCLO6_AxDischBlt_Main | 36301004 | Switched off | The motor has been switched off temporarily.
| GAPCLO6_AxBlt1_Main | 36302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO6_AxBlt1_Main | 36302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO6_AxBlt1_Main | 36302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO6_AxBlt1_Main | 36302003 | Validation fault | The module detected a value out of range.
| GAPCLO6_AxBlt1_Main | 36302004 | Switched off | The motor has been switched off temporarily.
| GAPCLO6_AxBlt2_Main | 36303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO6_AxBlt2_Main | 36303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO6_AxBlt2_Main | 36303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO6_AxBlt2_Main | 36303003 | Validation fault | The module detected a value out of range.
| GAPCLO6_AxBlt2_Main | 36303004 | Switched off | The motor has been switched off temporarily.
| GAPCLO7_SM_Main | 37010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO7_SM_Main | 37010002 | Calculation active | The unit is in calculation state.
| GAPCLO7_SM_Main | 37010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLO7_SM_Main | 37010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLO7_Saf_Main | 37020060 | Energize drives fault | The energizing of the drive is faulted.
| FXX7_AxTranspBlt1_Main | 37201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX7_AxTranspBlt1_Main | 37201001 | Position error | The controlled motor is out of the commanded position.
| FXX7_AxTranspBlt1_Main | 37201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX7_AxTranspBlt1_Main | 37201003 | Validation fault | The module detected a value out of range.
| FXX7_AxTranspBlt1_Main | 37201004 | Switched off | The motor has been switched off temporarily.
| FXX7_AxTranspBlt2_Main | 37202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX7_AxTranspBlt2_Main | 37202001 | Position error | The controlled motor is out of the commanded position.
| FXX7_AxTranspBlt2_Main | 37202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX7_AxTranspBlt2_Main | 37202003 | Validation fault | The module detected a value out of range.
| FXX7_AxTranspBlt2_Main | 37202004 | Switched off | The motor has been switched off temporarily.
| FXX7_AxTranspBlt3_Main | 37203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXX7_AxTranspBlt3_Main | 37203001 | Position error | The controlled motor is out of the commanded position.
| FXX7_AxTranspBlt3_Main | 37203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXX7_AxTranspBlt3_Main | 37203003 | Validation fault | The module detected a value out of range.
| FXX7_AxTranspBlt3_Main | 37203004 | Switched off | The motor has been switched off temporarily.
| GAPCLO7_Ctr_Main | 37300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLO7_Ctr_Main | 37300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLO7_Ctr_Main | 37300002 | Homing active | The feeding system is homing or synchronising
| GAPCLO7_AxDischBlt_Main | 37301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO7_AxDischBlt_Main | 37301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO7_AxDischBlt_Main | 37301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO7_AxDischBlt_Main | 37301003 | Validation fault | The module detected a value out of range.
| GAPCLO7_AxDischBlt_Main | 37301004 | Switched off | The motor has been switched off temporarily.
| GAPCLO7_AxBlt1_Main | 37302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO7_AxBlt1_Main | 37302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO7_AxBlt1_Main | 37302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO7_AxBlt1_Main | 37302003 | Validation fault | The module detected a value out of range.
| GAPCLO7_AxBlt1_Main | 37302004 | Switched off | The motor has been switched off temporarily.
| GAPCLO7_AxBlt2_Main | 37303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLO7_AxBlt2_Main | 37303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLO7_AxBlt2_Main | 37303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLO7_AxBlt2_Main | 37303003 | Validation fault | The module detected a value out of range.
| GAPCLO7_AxBlt2_Main | 37303004 | Switched off | The motor has been switched off temporarily.
| GAPCLOR_SM_Main | 40010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLOR_SM_Main | 40010002 | Calculation active | The unit is in calculation state.
| GAPCLOR_SM_Main | 40010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| GAPCLOR_SM_Main | 40010005 | Clean mode unit is active | The unit clean mode is active.
| SFT_GAPCLOR_Saf_Main | 40020060 | Energize drives fault | The energizing of the drive is faulted.
| FXXR_AxTranspBlt1_Main | 40201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXXR_AxTranspBlt1_Main | 40201001 | Position error | The controlled motor is out of the commanded position.
| FXXR_AxTranspBlt1_Main | 40201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXXR_AxTranspBlt1_Main | 40201003 | Validation fault | The module detected a value out of range.
| FXXR_AxTranspBlt1_Main | 40201004 | Switched off | The motor has been switched off temporarily.
| FXXR_AxTranspBlt2_Main | 40202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXXR_AxTranspBlt2_Main | 40202001 | Position error | The controlled motor is out of the commanded position.
| FXXR_AxTranspBlt2_Main | 40202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXXR_AxTranspBlt2_Main | 40202003 | Validation fault | The module detected a value out of range.
| FXXR_AxTranspBlt2_Main | 40202004 | Switched off | The motor has been switched off temporarily.
| FXXR_AxTranspBlt3_Main | 40203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| FXXR_AxTranspBlt3_Main | 40203001 | Position error | The controlled motor is out of the commanded position.
| FXXR_AxTranspBlt3_Main | 40203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| FXXR_AxTranspBlt3_Main | 40203003 | Validation fault | The module detected a value out of range.
| FXXR_AxTranspBlt3_Main | 40203004 | Switched off | The motor has been switched off temporarily.
| GAPCLOR_Ctr_Main | 40300000 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
| GAPCLOR_Ctr_Main | 40300001 | A part is not homed | The home procedure has not been carried out yet.
| GAPCLOR_Ctr_Main | 40300002 | Homing active | The feeding system is homing or synchronising
| GAPCLOR_AxDischBlt_Main | 40301000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLOR_AxDischBlt_Main | 40301001 | Position error | The controlled motor is out of the commanded position.
| GAPCLOR_AxDischBlt_Main | 40301002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLOR_AxDischBlt_Main | 40301003 | Validation fault | The module detected a value out of range.
| GAPCLOR_AxDischBlt_Main | 40301004 | Switched off | The motor has been switched off temporarily.
| GAPCLOR_AxBlt1_Main | 40302000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLOR_AxBlt1_Main | 40302001 | Position error | The controlled motor is out of the commanded position.
| GAPCLOR_AxBlt1_Main | 40302002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLOR_AxBlt1_Main | 40302003 | Validation fault | The module detected a value out of range.
| GAPCLOR_AxBlt1_Main | 40302004 | Switched off | The motor has been switched off temporarily.
| GAPCLOR_AxBlt2_Main | 40303000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| GAPCLOR_AxBlt2_Main | 40303001 | Position error | The controlled motor is out of the commanded position.
| GAPCLOR_AxBlt2_Main | 40303002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| GAPCLOR_AxBlt2_Main | 40303003 | Validation fault | The module detected a value out of range.
| GAPCLOR_AxBlt2_Main | 40303004 | Switched off | The motor has been switched off temporarily.
| DDU1_GMS_Main | 41004000 | Circuit breaker drive control voltage | The circuit breaker is switched off.
| DDU1_GMS_Main | 41004001 | Circuit breaker belt tracking control voltage | The circuit breaker is switched off.
| DDU1_GMS_Main | 41004002 | Converter fault | The converter is reporting a fault.
| DDU1_SM_Main | 41010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
| DDU1_SM_Main | 41010001 | Service mode active | The unit is in service mode. No production active.
| DDU1_SM_Main | 41010002 | Calculation active | The unit is in calculation state.
| DDU1_SM_Main | 41010003 | Unit switched off | The unit is disabled.
| DDU1_SM_Main | 41010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
| SFT_DDU1_Saf | 41020010 | Door left 1 open | There is a guard on the machine which is open.
| SFT_DDU1_Saf | 41020011 | Door left 2 open | There is a guard on the machine which is open.
| SFT_DDU1_Saf | 41020012 | Door right 1 open | There is a guard on the machine which is open.
| SFT_DDU1_Saf | 41020013 | Door right 2 open | There is a guard on the machine which is open.
| DDU1_Saf_Cov | 41020018 | Doors open requested | The guard will be opened as soon as the last move is done.
| SFT_DDU1_Saf | 41020060 | Energize drive fault Diverter | The energizing of the drive is faulted.
| DDU1_Saf_Air_MS6SV | 41020090 | Exhaust valve fault | The exhaust valve has a fault.
| DDU1_Saf_Air_MS6SV | 41020091 | Restarting exhaust valve | The exhaust valve is restarting.
| SFT_DDU1_Saf | 41020092 | Energize exhaust valve fault | The energizing of the valve is faulted.
| DDU1_Saf_Air_HEED | 41020093 | Air pressure too low | The air pressure is below the allowed operating level.
| DDU1_Saf_Air_HEED | 41020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
| DDU1_Ctr_Main | 41200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
| DDU1_Ctr_Main | 41200002 | Dump unit home needed | The dump unit is stopping to home after restart.
| DDU1_Ctr_Main | 41200003 | Manual dumping active | The manual dumping is active.
| DDU1_Ctr_Main | 41200004 | Remove all rows from diverter head | After emergency stop or fault, all products have to be removed from the diverter head. Opening and closing the guard of the unit when removing the products will automatically reset this message.
| DDU1_Ctr_Main | 41200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
| DDU1_Ctr_Md | 41200007 | Row with metal detected | Metaldetector has a row (rows) with metal detected
| DDU1_Ctr_Md | 41200008 | Metal reject box full | Metal reject box full
| DDU1_Ctr_Camera | 41200011 | Vision camera not ready | Vision camera is not ready.
| DDU1_Ctr_Camera | 41200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
| DDU1_Ctr_Main | 41200014 | Too many rows in register | There are too many rows between the photoeye and the move position of the diverter.
| DDU1_Ctr_Main | 41200014 | Too many rows in register | There are too many rows between the photoeye and the move position of the pullnose.
| DDU1_Ctr_Main | 41200015 | Photoeye row detection not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DDU1_Ctr_Main | 41200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
| DDU1_Ctr_Main | 41200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
| DDU1_Ctr_Main | 41200020 | Diverter invalid position parameter | The distance between the dump- and the pass position is more than 180 degrees.
| DDU1_Ctr_Main | 41200030 | Pullnose invalid position parameter | The distance between the open- and the close position is more than 180 degrees.
| DDU1_Ctr_Main | 41200031 | Pullnose open speed profile not valid | Acceleration and deceleration to open the pullnose are too low or the speed is less than the speed of the belt.
| DDU1_Ctr_Main | 41200032 | Pullnose close speed profile not valid | Parameter for maximum speed or calculated speed to close the pullnose is less than the belt speed or the calculated deceleration is too high.
| DDU1_Ctr_Md | 41200050 | Metaldetector not ready | The metaldetector which is usually required to operate the system under normal circumstances is not ready (initalization active, faulty or turned off locally).
| DDU1_Ctr_Md | 41200051 | Metaldetector overload | Overload metaldetector.
| DDU1_AxDivr_Main | 41203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DDU1_AxDivr_Main | 41203001 | Position error | The controlled motor is out of the commanded position.
| DDU1_AxDivr_Main | 41203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DDU1_AxDivr_Main | 41203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DDU1_AxDivr_Main | 41203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DDU1_AxDivr_Main | 41203006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
| DDU1_AxDivr_Main | 41203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| DDU1_AxDivr_Main | 41203023 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
| DDU1_AxPuln_Main | 41204000 | Drive fault | The drive controller of this motor is reporting a fault condition.
| DDU1_AxPuln_Main | 41204001 | Position error | The controlled motor is out of the commanded position.
| DDU1_AxPuln_Main | 41204002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
| DDU1_AxPuln_Main | 41204003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
| DDU1_AxPuln_Main | 41204004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
| DDU1_AxPuln_Main | 41204006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
| DDU1_AxPuln_Main | 41204010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
| H1_SMCtr_Main_DXX/DAX | 61009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| H1_SMCtr_Main_DXX/DAX | 61009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| H2_SMCtr_Main_DXX/DAX | 62009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| H2_SMCtr_Main_DXX/DAX | 62009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| H3_SMCtr_Main_DXX/DAX | 63009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| H3_SMCtr_Main_DXX/DAX | 63009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| H4_SMCtr_Main_DXX/DAX | 64009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| H4_SMCtr_Main_DXX/DAX | 64009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| H5_SMCtr_Main_DXX/DAX | 65009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| H5_SMCtr_Main_DXX/DAX | 65009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| H6_SMCtr_Main_DXX/DAX | 66009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| H6_SMCtr_Main_DXX/DAX | 66009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| H7_SMCtr_Main_DXX/DAX | 67009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| H7_SMCtr_Main_DXX/DAX | 67009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| HR_SMCtr_Main_DXX/DAX | 70009000 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
| HR_SMCtr_Main_DXX/DAX | 70009001 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
| INFO_Main |  | No SD card | The SD card in the controller is missing
| INFO_Main |  | SD card write error | The Prozessor has a problem to write the datas to the SD card
| INFO_Main |  | SD card read error | The Prozessor has a problem to read the datas from the SD card
Data# | Processor Tag |  | Value | Concentrator Tag | Path IP | Description | Python Variable Name
1 | [DBS080]UIFACE_b_oHOLReady |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.32 | Belt Head of Line Ready
2 | [DBS080]UIFACE_b_oLineReady |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].1 | 10.168.100.32 | Line Ready
3 | [DBS080]BLTHOL_AxDdu1_Iface.b_RunInProd |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].2 | 10.168.100.32 | DDU1 In Production Mode
4 | [DBS080]BLTHOL_AxU1_Iface.b_RunInProd |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].3 | 10.168.100.32 | U1 In Production Mode
5 | [DBS080]BLTHOL_AxU2_Iface.b_RunInProd |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].4 | 10.168.100.32 | U2 In Production Mode
6 | [DBS080]BLTHOL_AxU3_Iface.b_RunInProd |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].5 | 10.168.100.32 | U3 In Production Mode
7 | [DBS080]BLTHOL_AxU4_Iface.b_RunInProd |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].6 | 10.168.100.32 | U4 In Production Mode
8 | [DBS080]BLT_AxDu1_Iface.b_RunInProd |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].7 | 10.168.100.32 | DU1 In Production Mode
9 | [DBS080]BLT_AxDu2_Iface.b_RunInProd |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].8 | 10.168.100.32 | DU2 In Production Mode
10 | [DBS080]BLT_SM_Iface.dnError >65536 OR [DBS080]BLTHOL_SM_Iface.dnError .65536 |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].9 | 10.168.100.32 | Fault Present
11 | [DBS080]CtrlIface.b_AlarmActive |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].10 | 10.168.100.32 | Alarm Present
12 | [DBS080]HMI_Cmd.BtnEnShift1.b_Active |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].11 | 10.168.100.32 | Shift 1 Enabled
13 | [DBS080]HMI_Cmd.BtnEnShift2.b_Active |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].12 | 10.168.100.32 | Shift 2 Enabled
14 | [DBS080]HMI_Cmd.BtnEnShift3.b_Active |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[0].13 | 10.168.100.32 | Shift 3 Enabled
15
16 | [DBS080]INFO_Hmi.ProdCounter.dn_RowInfeed |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.32 | Rows into DBS | dbs_080_row_count_into_system
17 | [DBS080]INFO_Hmi.StatisticsCounter.dn_RowManualDump |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[11] | 10.168.100.32 | Rows Manually Dumped | dbs_080_rows_manually_dumped
18 | [DBS080]INFO_Hmi.StatisticsCounter.dn_RowTooSmall |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.32 | Rows Dumped Row Too Small | dbs_080_rows_dumped_row_too_small
19 | [DBS080]INFO_Hmi.StatisticsCounter.dn_RowTooLong |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[13] | 10.168.100.32 | Rows Dumped Row Too Long | dbs_080_rows_dumped_row_too_long
20 | [DBS080]INFO_Hmi.StatisticsCounter.dn_RowTooHigh |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[14] | 10.168.100.32 | Rows Dumped Row Too High | dbs_080_rows_dumped_row_too_high
21 | [DBS080]INFO_Hmi.StatisticsCounter.dn_GapTooSmall |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[15] | 10.168.100.32 | Rows Dumped Gap Too Small | dbs_080_rows_dumped_gap_too_small
22 | [DBS080]INFO_Hmi.StatisticsCounter.dn_RowPosNotValid |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[16] | 10.168.100.32 | Rows Dumped Row Out of Position | dbs_080_rows_dumped_row_out_of_position
23 | [DBS080]INFO_Hmi.StatisticsCounter.dn_DwnstrNotReady |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[17] | 10.168.100.32 | Rows Dumped Downstream Not Ready | dbs_080_rows_dumped_downstream_not_ready
24 | [DBS080]INFO_Hmi.StatisticsCounter.dn_NotRun |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.32 | Rows Dumped Not in Run | dbs_080_rows_dumped_not_in_run
25 | [DBS080]INFO_Hmi.ProdCounter.dn_RowDistribDu1 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.32 | Rows Distributed to Handpack 1 | dbs_080_rows_distributed_to_packing_leg_1
26 | [DBS080]INFO_Hmi.ProdCounter.dn_RowDistribDu2 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[20] | 10.168.100.32 | Rows Distributed to Handpack 2 | dbs_080_rows_distributed_to_packing_leg_2
| [DBS080]DA_Ctr_Iface.dn_FillingLevelPercent |  | Var | ComData_DBS_080_Alpha_To_Skynet.Status_Bits[22] | 10.168.100.32 | Buffer Fill Level
27 | [DBS080]HMI_Cmd.Dn_StartHoursShift1 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[0] | 10.168.100.32 | Start Time Hours Shift 1
28 | [DBS080]HMI_Cmd.Dn_StartMinutesShift1 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[1] | 10.168.100.32 | Start Time Minutes Shift 1
29 | [DBS080]HMI_Cmd.Dn_StartHoursShift2 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[2] | 10.168.100.32 | Start Time Hours Shift 2
30 | [DBS080]HMI_Cmd.Dn_StartMinutesShift2 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[3] | 10.168.100.32 | Start Time Minutes Shift 2
31 | [DBS080]HMI_Cmd.Dn_StartHoursShift3 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[4] | 10.168.100.32 | Start Time Hours Shift 3
32 | [DBS080]HMI_Cmd.Dn_StartMinutesShift3 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[5] | 10.168.100.32 | Start Time Minutes Shift 3
33 | [DBS080]HMI_Cmd.Dn_EndHoursShift1 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[6] | 10.168.100.32 | End Time Hours Shift 1
34 | [DBS080]HMI_Cmd.Dn_EndMinutesShift1 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[7] | 10.168.100.32 | End Time Minutes Shift 1
35 | [DBS080]HMI_Cmd.Dn_EndHoursShift2 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[8] | 10.168.100.32 | End Time Hours Shift 2
36 | [DBS080]HMI_Cmd.Dn_EndMinutesShift2 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[9] | 10.168.100.32 | End Time Minutes Shift 2
37 | [DBS080]HMI_Cmd.Dn_EndHoursShift3 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[10] | 10.168.100.32 | End Time Hours Shift 3
38 | [DBS080]HMI_Cmd.Dn_EndMinutesShift3 |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[11] | 10.168.100.32 | End Time Minutes Shift 3
36 | [DBS080]HMI_dn_Hour |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[12] | 10.168.100.32 | Current Hour In Processor
37 | [DBS080]HMI_dn_Minute |  | Var | ComData_DBS_080_Alpha_To_Skynet.Parameters[13] | 10.168.100.32 | Current Minute In Processor
38 | [DBS080]SM.Errors.DynText.List[0].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[0] | 10.168.100.32 | Dynamic Text Fault List 0
39 | [DBS080]SM.Errors.DynText.List[1].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[1] | 10.168.100.32 | Dynamic Text Fault List 1
40 | [DBS080]SM.Errors.DynText.List[2].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[2] | 10.168.100.32 | Dynamic Text Fault List 2
41 | [DBS080]SM.Errors.DynText.List[3].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[3] | 10.168.100.32 | Dynamic Text Fault List 3
42 | [DBS080]SM.Errors.DynText.List[4].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[4] | 10.168.100.32 | Dynamic Text Fault List 4
43 | [DBS080]SM.Errors.DynText.List[5].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[5] | 10.168.100.32 | Dynamic Text Fault List 5
44 | [DBS080]SM.Errors.DynText.List[6].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[6] | 10.168.100.32 | Dynamic Text Fault List 6
45 | [DBS080]SM.Errors.DynText.List[7].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[7] | 10.168.100.32 | Dynamic Text Fault List 7
46 | [DBS080]SM.Errors.DynText.List[8].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[8] | 10.168.100.32 | Dynamic Text Fault List 8
47 | [DBS080]SM.Errors.DynText.List[9].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[9] | 10.168.100.32 | Dynamic Text Fault List 9
48 | [DBS080]SM.Errors.DynText.List[10].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[10] | 10.168.100.32 | Dynamic Text Fault List 10
49 | [DBS080]SM.Errors.DynText.List[11].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[11] | 10.168.100.32 | Dynamic Text Fault List 11
50 | [DBS080]SM.Errors.DynText.List[12].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[12] | 10.168.100.32 | Dynamic Text Fault List 12
51 | [DBS080]SM.Errors.DynText.List[13].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[13] | 10.168.100.32 | Dynamic Text Fault List 13
52 | [DBS080]SM.Errors.DynText.List[14].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[14] | 10.168.100.32 | Dynamic Text Fault List 14
53 | [DBS080]SM.Errors.DynText.List[15].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[15] | 10.168.100.32 | Dynamic Text Fault List 15
54 | [DBS080]SM.Errors.DynText.List[16].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[16] | 10.168.100.32 | Dynamic Text Fault List 16
55 | [DBS080]SM.Errors.DynText.List[17].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[17] | 10.168.100.32 | Dynamic Text Fault List 17
56 | [DBS080]SM.Errors.DynText.List[18].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[18] | 10.168.100.32 | Dynamic Text Fault List 18
57 | [DBS080]SM.Errors.DynText.List[19].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[19] | 10.168.100.32 | Dynamic Text Fault List 19
58 | [DBS080]SM.Errors.DynText.List[20].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[20] | 10.168.100.32 | Dynamic Text Fault List 20
59 | [DBS080]SM.Errors.DynText.List[21].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[21] | 10.168.100.32 | Dynamic Text Fault List 21
60 | [DBS080]SM.Errors.DynText.List[22].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[22] | 10.168.100.32 | Dynamic Text Fault List 22
61 | [DBS080]SM.Errors.DynText.List[23].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[23] | 10.168.100.32 | Dynamic Text Fault List 23
62 | [DBS080]SM.Errors.DynText.List[24].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[24] | 10.168.100.32 | Dynamic Text Fault List 24
63 | [DBS080]SM.Errors.DynText.List[25].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[25] | 10.168.100.32 | Dynamic Text Fault List 25
64 | [DBS080]SM.Errors.DynText.List[26].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[26] | 10.168.100.32 | Dynamic Text Fault List 26
65 | [DBS080]SM.Errors.DynText.List[27].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[27] | 10.168.100.32 | Dynamic Text Fault List 27
66 | [DBS080]SM.Errors.DynText.List[28].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[28] | 10.168.100.32 | Dynamic Text Fault List 28
67 | [DBS080]SM.Errors.DynText.List[29].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[29] | 10.168.100.32 | Dynamic Text Fault List 29
68 | [DBS080]SM.Errors.FixText.List[0].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[30] | 10.168.100.32 | Fixed Text Fault List 0
69 | [DBS080]SM.Errors.FixText.List[1].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[31] | 10.168.100.32 | Fixed Text Fault List 1
70 | [DBS080]SM.Errors.FixText.List[2].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[32] | 10.168.100.32 | Fixed Text Fault List 2
71 | [DBS080]SM.Errors.FixText.List[3].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[33] | 10.168.100.32 | Fixed Text Fault List 3
72 | [DBS080]SM.Errors.FixText.List[4].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[34] | 10.168.100.32 | Fixed Text Fault List 4
73 | [DBS080]SM.Errors.FixText.List[5].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[35] | 10.168.100.32 | Fixed Text Fault List 5
74 | [DBS080]SM.Errors.FixText.List[6].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[36] | 10.168.100.32 | Fixed Text Fault List 6
75 | [DBS080]SM.Errors.FixText.List[7].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[37] | 10.168.100.32 | Fixed Text Fault List 7
76 | [DBS080]SM.Errors.FixText.List[8].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[38] | 10.168.100.32 | Fixed Text Fault List 8
77 | [DBS080]SM.Errors.FixText.List[9].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[39] | 10.168.100.32 | Fixed Text Fault List 9
78 | [DBS080]SM.Errors.FixText.List[10].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[40] | 10.168.100.32 | Fixed Text Fault List 10
79 | [DBS080]SM.Errors.FixText.List[11].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[41] | 10.168.100.32 | Fixed Text Fault List 11
80 | [DBS080]SM.Errors.FixText.List[12].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[42] | 10.168.100.32 | Fixed Text Fault List 12
81 | [DBS080]SM.Errors.FixText.List[13].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[43] | 10.168.100.32 | Fixed Text Fault List 13
82 | [DBS080]SM.Errors.FixText.List[14].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[44] | 10.168.100.32 | Fixed Text Fault List 14
83 | [DBS080]SM.Errors.FixText.List[15].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[45] | 10.168.100.32 | Fixed Text Fault List 15
84 | [DBS080]SM.Errors.FixText.List[16].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[46] | 10.168.100.32 | Fixed Text Fault List 16
85 | [DBS080]SM.Errors.FixText.List[17].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[47] | 10.168.100.32 | Fixed Text Fault List 17
86 | [DBS080]SM.Errors.FixText.List[18].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[48] | 10.168.100.32 | Fixed Text Fault List 18
87 | [DBS080]SM.Errors.FixText.List[19].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[49] | 10.168.100.32 | Fixed Text Fault List 19
88 | [DBS080]SM.Errors.FixText.List[20].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[50] | 10.168.100.32 | Fixed Text Fault List 20
89 | [DBS080]SM.Errors.FixText.List[21].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[51] | 10.168.100.32 | Fixed Text Fault List 21
90 | [DBS080]SM.Errors.FixText.List[22].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[52] | 10.168.100.32 | Fixed Text Fault List 22
91 | [DBS080]SM.Errors.FixText.List[23].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[53] | 10.168.100.32 | Fixed Text Fault List 23
92 | [DBS080]SM.Errors.FixText.List[24].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[54] | 10.168.100.32 | Fixed Text Fault List 24
93 | [DBS080]SM.Errors.FixText.List[25].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[55] | 10.168.100.32 | Fixed Text Fault List 25
94 | [DBS080]SM.Errors.FixText.List[26].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[56] | 10.168.100.32 | Fixed Text Fault List 26
95 | [DBS080]SM.Errors.FixText.List[27].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[57] | 10.168.100.32 | Fixed Text Fault List 27
96 | [DBS080]SM.Errors.FixText.List[28].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[58] | 10.168.100.32 | Fixed Text Fault List 28
97 | [DBS080]SM.Errors.FixText.List[29].dn_ID |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[59] | 10.168.100.32 | Fixed Text Fault List 29
98 | [DBS080]SM.Errors.DynText.dn_LastPos |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[60] | 10.168.100.32 | Position of Last stored position in Dyn List
99 | [DBS080]SM.Errors.FixText.dn_LastPos |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[61] | 10.168.100.32 | Position of Last stored position in Fix List
100 | [DBS080]SM.Errors.DynText.dn_EmptyPos |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[62] | 10.168.100.32 | Position of Next stored position in Dyn List
101 | [DBS080]SM.Errors.FixText.dn_EmptyPos |  | Var | ComData_DBS_080_Alpha_To_Skynet.Fault_data[63] | 10.168.100.32 | Position of Next stored position in Fix List
110 | [DBS080]BLTHOL_Du2Track_ErrIface.b_OutOfRange |  | 256 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].8 | 10.168.100.32 | Du2 Belt Tracking Fault
109 | [DBS080]BLTHOL_Du2Track_b_BltOutOfPos |  | 128 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].7 | 10.168.100.32 | Du2 Belt Tracking Warning
108 | [DBS080]BLTHOL_Du1Track_ErrIface.b_OutOfRange |  | 64 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].6 | 10.168.100.32 | Du1 Belt Tracking Fault
107 | [DBS080]BLTHOL_Du1Track_b_BltOutOfPos |  | 32 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].5 | 10.168.100.32 | Du1 Belt Tracking Warning
106 | [DBS080]BLTHOL_Ddu1Track_ErrIface.b_OutOfRange |  | 16 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].4 | 10.168.100.32 | DDu1 Belt Tracking Fault
105 | [DBS080]BLTHOL_Ddu1Track_b_BltOutOfPos |  | 8 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].3 | 10.168.100.32 | DDU1 Belt Tracking Warning
104 | [DBS080]BLTHOL_U4Track_i_Supervision |  | 4 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].2 | 10.168.100.32 | Belt 4 Tracking Fault
103 | [DBS080]BLTHOL_U3Track_i_Supervision |  | 2 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].1 | 10.168.100.32 | Belt 3 Tracking Fault
102 | [DBS080]BLTHOL_U1Track_i_Supervision |  | 1 | ComData_DBS_080_Alpha_To_Skynet.Fault_data[80].0 | 10.168.100.32 | Belt 1 Tracking Fault

## Alpha DFR 031
HMI Fault Messages:
# | Component | Fault Value | Error Text | Description
1 | SMCtr | 1001000 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI. |  |  |  | 1 | [DFR031]SM_Ctr_ErrIface.b_SystemInitActive | 1 | 10.168.100.32 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
2 | SMCtr | 1001001 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 2 | [DFR031]SM_Ctr_ErrIface.b_InitTimeout | 1 | 10.168.100.32 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
3 | SMCtr | 1001002 | Too small | This is a system failure: the shown registration list is too small. |  |  |  | 3 | [DFR031]SM_Ctr_ErrIface.b_ListTooSmall | 1 | 10.168.100.32 | Too small | This is a system failure: the shown registration list is too small.
4 | SMCtr | 1001003 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module. |  |  |  | 4 | [DFR031]SM_Ctr_ErrIface.b_ModuleRegError | 1 | 10.168.100.32 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
5 | SMCtr | 1001004 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines. |  |  |  | 5 | [DFR031]SM_Ctr_ErrIface.b_ErrorListWasFull | 1 | 10.168.100.32 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
6 | SMCtr | 1001005 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing. |  |  |  | 6 | [DFR031]SM_Ctr_ErrIface.b_StateAckFault | 1 | 10.168.100.32 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
7 | SMCtr | 1001006 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault. |  |  |  | 7 | [DFR031]SM_Ctr_ErrIface.b_ErrorRegFault | 1 | 10.168.100.32 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
8 | SMCtr | 1001007 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on. |  |  |  | 8 | [DFR031]SM_Ctr_ErrIface.b_PowerDownActive | 1 | 10.168.100.32 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
9 | SMCtr | 1001008 | Controller Timeout | Global Statemachine fault. |  |  |  | 9 | [DFR031]SM_Ctr_ErrIface.b_ControllerTimeout | 1 | 10.168.100.32 | Controller Timeout | Global Statemachine fault.
10 | SMCtr | 1001009 | Controller registration fault | This is a system failure: the controller identification is defined wrong. |  |  |  | 10 | [DFR031]SM_Ctr_ErrIface.b_CIFRegError | 1 | 10.168.100.32 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
11 | SMCtr | 1001010 | State machine init - | This is a system failure. |  |  |  | 11 | [DFR031]SM_Ctr_ErrIface.b_SMRegError | 1 | 10.168.100.32 | State machine init - | This is a system failure.
12 | SMCtr | 1001011 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module. |  |  |  | 12 | [DFR031]SM_Ctr_ErrIface.b_UndefErrorOnHMI | 1 | 10.168.100.32 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
13 | HMI | 1002000 | Data transfer active | Data is being sent to the controller. This message will disappear automatically. |  |  |  | 13 | [DFR031]HMI_ErrIface.b_DownloadActive | 1 | 10.168.100.32 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
14 | CPU | 1003000 | Battery low | The voltage of the internal battery of the PLC is low. |  |  |  | 14 | [DFR031]CPU_ErrIface.b_BatteryLow | 1 | 10.168.100.32 | Battery low | The voltage of the internal battery of the PLC is low.
15 | CPU | 1003005 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout. |  |  |  | 15 | [DFR031]CPU_ErrIface.b_HmiComError | 1 | 10.168.100.32 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout.
16 | GMS | 1004010 | Air conditioner message |  |  |  |  | 16 | [DFR031]GMS_ErrIface.b_NoCompAir | 1 | 10.168.100.32 | Air pressure too low | The air pressure is below the allowed operating level.
17 | GMS | 1004011 | Circuit breaker air conditioner | The circuit breaker is switched off. |  |  |  | 17 | [DFR031]GMS_ErrIface.b_AirConditionerMessage | 1 | 10.168.100.32 | Air conditioner message
18 | GMS | 1004021 | Circuit breaker branch control voltage | The circuit breaker is switched off. |  |  |  | 18 | [DFR031]GMS_ErrIface.b_AirConditionerCircBreaker | 1 | 10.168.100.32 | Circuit breaker air conditioner | The circuit breaker is switched off.
19 | GMS | 1004022 | Circuit breaker branch main power Kinetix Racks | The circuit breaker is switched off. |  |  |  | 19 | [DFR031]GMS_ErrIface.b_CircBreakBranchContrVoltage | 1 | 10.168.100.32 | Circuit breaker branch control voltage | The circuit breaker is switched off.
20 | GMS | 1004023 | Circuit breaker control voltage | The circuit breaker is switched off. |  |  |  | 20 | [DFR031]GMS_ErrIface.b_CircBreakBranchMainPwrKinetixRacks | 1 | 10.168.100.32 | Circuit breaker branch main power Kinetix Racks | The circuit breaker is switched off.
21 | GMS | 1004024 | Circuit breaker main power Kinetix Racks | The circuit breaker is switched off. |  |  |  | 21 | [DFR031]GMS_ErrIface.b_CircBreakContrVoltage | 1 | 10.168.100.32 | Circuit breaker control voltage | The circuit breaker is switched off.
22 | GMS | 1004025 | Circuit breaker auxiliary power Kinetix Racks | The circuit breaker is switched off. |  |  |  | 22 | [DFR031]GMS_ErrIface.b_CircBreakMainPwrKinetixRacks | 1 | 10.168.100.32 | Circuit breaker main power Kinetix Racks | The circuit breaker is switched off.
23 | IO | 1005001 | Electronic fuse triggered on 2A digital output card | The electronic protection circuit of one the of digital output cards for 2A high power outputs of the PLC has been activated due to a short circuit. |  |  |  | 23 | [DFR031]GMS_ErrIface.b_CircBreakAuxPwrKinetixRacks | 1 | 10.168.100.32 | Circuit breaker auxiliary power Kinetix Racks | The circuit breaker is switched off.
24 | IO | 1005010 | Missing I/O Rack 0 (cabinet) | One of the I/O modules is missing. |  |  |  | 24 | [DFR031]IO_ErrIface.b_FuseBlownDigitalOutputs | 1 | 10.168.100.32 | Electronic fuse triggered on 2A digital output card | The electronic protection circuit of one the of digital output cards for 2A high power outputs of the PLC has been activated due to a short circuit.
25 | IO | 1005011 | DDU1: Missing remote I/O | One of the Remote I/O modules is missing. |  |  |  | 25 | [DFR031]IO_ErrIface.b_MissingRemoteIOCabinet | 1 | 10.168.100.32 | Missing I/O Rack 0 (cabinet) | One of the I/O modules is missing.
26 | IO | 1005029 | Buffer: Missing remote I/O | One of the Remote I/O modules is missing. |  |  |  | 26 | [DFR031]IO_ErrIface.b_MissingRemoteIODdu1 | 1 | 10.168.100.32 | DDU1: Missing remote I/O | One of the Remote I/O modules is missing.
27 | SAF | 1020006 | LOTO switch main cabinet turned off | The Lock Out Tag Out (LOTO) switch at main cabinet is turned off. |  |  |  | 27 | [DFR031]IO_ErrIface.b_MissingRemoteIOBuffer | 1 | 10.168.100.32 | Buffer: Missing remote I/O | One of the Remote I/O modules is missing.
28 | SAF | 1020010 | Emergency stop cabinet | The emergency stop button is pressed or has already been disengaged. |  |  |  | 28 | [DFR031]INFO_ErrIface.b_SDCard_NotPresent | 1 | 10.168.100.32 | No SD card | The SD card in the controller is missing
29 | SAF | 1020011 | Emergency stop buffer discharge panel | The emergency stop button is pressed or has already been disengaged. |  |  |  | 29 | [DFR031]INFO_ErrIface.b_SDCard_WriteErr | 1 | 10.168.100.32 | SD card write error | The Prozessor has a problem to write the datas to the SD card
30 | SAF | 1020012 | Emergency stop buffer discharge | The emergency stop button is pressed or has already been disengaged. |  |  |  | 30 | [DFR031]INFO_ErrIface.b_SDCard_ReadErr | 1 | 10.168.100.32 | SD card read error | The Prozessor has a problem to read the datas from the SD card
31 | SAF | 1020013 | Emergency stop buffer infeed left | The emergency stop button is pressed or has already been disengaged. |  |  |  | 31 | [DFR031]SAF_ErrIface.b_LoToSwitchOff | 1 | 10.168.100.32 | LOTO switch main cabinet turned off | The Lock Out Tag Out (LOTO) switch at main cabinet is turned off.
32 | SAF | 1020014 | Emergency stop buffer infeed right | The emergency stop button is pressed or has already been disengaged. |  |  |  | 32 | [DFR031]SFT_SAF_ErrIface.EmStopCabinet.b_DeEnergized | 1 | 10.168.100.32 | Emergency stop cabinet | The emergency stop button is pressed or has already been disengaged.
33 | SAF | 1020015 | Emergency stop ALN1 left | The emergency stop button is pressed or has already been disengaged. |  |  |  | 33 | [DFR031]SFT_SAF_ErrIface.EmStopDadPanel.b_DeEnergized | 1 | 10.168.100.32 | Emergency stop buffer discharge panel | The emergency stop button is pressed or has already been disengaged.
34 | SAF | 1020016 | Emergency stop ALN1 right | The emergency stop button is pressed or has already been disengaged. |  |  |  | 34 | [DFR031]SFT_SAF_ErrIface.EmStopDad.b_DeEnergized | 1 | 10.168.100.32 | Emergency stop buffer discharge | The emergency stop button is pressed or has already been disengaged.
35 | Upstream Interface | 1030002 | Ethernet communication fault | An ethernet fault with the upstream system is active. |  |  |  | 35 | [DFR031]SFT_SAF_ErrIface.EmStopDaiLeft.b_DeEnergized | 1 | 10.168.100.32 | Emergency stop buffer infeed left | The emergency stop button is pressed or has already been disengaged.
36 | Upstream Interface | 1030010 | Interface disabled | The upstream interface is disabled. |  |  |  | 36 | [DFR031]SFT_SAF_ErrIface.EmStopDaiRight.b_DeEnergized | 1 | 10.168.100.32 | Emergency stop buffer infeed right | The emergency stop button is pressed or has already been disengaged.
37 | ALN1/SM | 11010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 37 | [DFR031]SFT_SAF_ErrIface.EmStopAln1Left.b_DeEnergized | 1 | 10.168.100.32 | Emergency stop ALN1 left | The emergency stop button is pressed or has already been disengaged.
38 | ALN1/SM | 11010001 | Service mode active | The aligner is in service mode. No aligning possible. |  |  |  | 38 | [DFR031]SFT_SAF_ErrIface.EmStopAln1Right.b_DeEnergized | 1 | 10.168.100.32 | Emergency stop ALN1 right | The emergency stop button is pressed or has already been disengaged.
39 | ALN1/SM | 11010002 | Calculation active | The unit is in calculation state. |  |  |  | 39 | [DFR031]UIFACE_ErrIface.b_ComFaultWithUpstream | 1 | 10.168.100.32 | Ethernet communication fault | An ethernet fault with the upstream system is active.
40 | ALN1/SM | 11010003 | Switched off | The aligner is disabled. |  |  |  | 40 | [DFR031]UIFACE_ErrIface.b_UifaceDisabled | 1 | 10.168.100.32 | Interface disabled | The upstream interface is disabled.
41 | ALN1/SM | 11010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 41 | [DFR031]BLTDAI_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
42 | ALN1/Saf | 11020010 | cover open | There is a guard on the machine which is open. |  |  |  | 42 | [DFR031]BLTDAI_SM_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | The process belts are in service mode. No production possible
43 | ALN1/Saf | 11020018 | cover open requested | The guard will be open if the last move is done. |  |  |  | 43 | [DFR031]BLTDAI_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
44 | ALN1/Saf | 11020060 | Energize drive fault | The energizing of the drive is faulted. |  |  |  | 44 | [DFR031]BLTDAI_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
45 | ALN1/Saf | 11020090 | Exhaust valve fault | The exhaust valve has a fault. |  |  |  | 45 | [DFR031]BLTDAI_SM_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode belts active | The process belts are in clean mode. No production possible.
46 | ALN1/Saf | 11020091 | Restarting exhaust valve | The exhaust valve is restarting. |  |  |  | 46 | [DFR031]BLTDAI_SM_ErrIface.b_EmptyModeActive | 1 | 10.168.100.32 | Empty mode belts is active | The belt empty mode is active.
47 | ALN1/Saf | 11020092 | Energize exhaust valve fault | The energizing of the valve is faulted. |  |  |  | 47 | [DFR031]SFT_BLTDAI_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
48 | ALN1/Saf | 11020093 | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 48 | [DFR031]BLTDAI_Saf_ErrIface.b_ExhaustValveFault | 1 | 10.168.100.32 | Exhaust valve fault | The exhaust valve has a fault.
49 | ALN1/Saf | 11020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system. |  |  |  | 49 | [DFR031]BLTDAI_Saf_ErrIface.b_RestartingExhaustValve | 1 | 10.168.100.32 | Restarting exhaust valve | The exhaust valve is restarting.
50 | ALN1 | 11200000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 50 | [DFR031]SFT_BLTDAI_Saf_ErrIface.EnergizeExhaustValve.b_DeEnergized | 1 | 10.168.100.32 | Energize exhaust valve fault | The energizing of the valve is faulted.
51 | ALN1 | 11200001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 51 | [DFR031]BLTDAI_Saf_ErrIface.b_NoCompAir | 1 | 10.168.100.32 | Air pressure too low | The air pressure is below the allowed operating level.
52 | ALN1 | 11200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 52 | [DFR031]BLTDAI_Saf_ErrIface.b_CompAirNotExhaust | 1 | 10.168.100.32 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
53 | ALN1 | 11200003 | Validation error | This is a validation error. One of the values is out of range. |  |  |  | 53 | [DFR031]BLTDAI_AxDai_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
54 | ALN1 | 11200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 54 | [DFR031]BLTDAI_AxDai_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
55 | ALN1 | 11200006 | Homing not possible | The motors of the aligner cannot be synchronized in the set time limit. |  |  |  | 55 | [DFR031]BLTDAI_AxDai_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
56 | ALN1 | 11200010 | Acc / Dec out of range | This is a validation error. Acceleration / deceleration out of range (bigger than maximum, or less than the minimum required to decelerate after aligning into the open position). |  |  |  | 56 | [DFR031]BLTDAI_AxDai_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
57 | ALN1 | 11200011 | Cycle time of the aligner too long | This is a validation error. The aligner needs too long for a cycle. Increase speeds and acc/dec to speed-up the aligner. |  |  |  | 57 | [DFR031]BLTDAI_AxDai_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
58 | ALN1 | 11200012 | Wrong aligner distance | This is a validation error. The aligner is too close to its start position. |  |  |  | 58 | [DFR031]BLTDAI_AxDai_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
59 | ALN1 | 11200013 | End move is too fast | This is a validation error. If the option clever aligning is on we have to move into the gap directly - without waiting in the open position. If the last move is too fast we would touch the rear edge of the row. |  |  |  | 59 | [DFR031]BLTDAI_AxDai_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
60 | ALN1 | 11200014 | Adjustment error | This is an adjustment error. One of the values is out of range. |  |  |  | 60 | [DFR031]BLTDAI_DaiTrack_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
61 | ALN1 | 11200016 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 61 | [DFR031]BLTDAI_DaiTrack_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
62 | ALN1 | 11200017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 62 | [DFR031]DA_SMCtr_ErrIface.b_EmptyModeActive | 1 | 10.168.100.32 | Mode empty active
63 | ALN1 | 11200018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed. |  |  |  | 63 | [DFR031]DA_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Mode clean active
64 | ALN1 | 11200019 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 64 | [DFR031]DA_SMCtr_ErrIface.b_FillModeActive | 1 | 10.168.100.32 | Mode fill active
65 | ALN1 | 11200020 | Home needed | The aligner is stopping to home after restart. |  |  |  | 65 | [DFR031]DA_LimitSwitch_ErrIface.b_TopEndSwitchMuted | 1 | 10.168.100.32 | Shuttle at top limit switch muted | The Shuttle is at the top limit switch and muted.
66 | ALN1 | 11200021 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast. |  |  |  | 66 | [DFR031]DA_LimitSwitch_ErrIface.b_BottomEndSwitchMuted | 1 | 10.168.100.32 | Shuttle at bottom limit switch muted | The Shuttle is at the bottom limit switch and muted.
67 | ALN1 | 11200022 | Product too high | There is a too high product detected in front of the aligner. |  |  |  | 67 | [DFR031]SFT_DA_LimitSwitch_ErrIface.TopEndSwitch.b_DeEnergized | 1 | 10.168.100.32 | Shuttle at top limit switch | The Shuttle is at the top limit switch.
68 | ALN1 | 11201004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 68 | [DFR031]SFT_DA_LimitSwitch_ErrIface.BottomEndSwitch.b_DeEnergized | 1 | 10.168.100.32 | Shuttle at bottom limit switch | The Shuttle is at the bottom limit switch.
69 | ALN1 | 11201016 | Warning photoeye is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 69 | [DFR031]SFT_DA_LimitSwitch_ErrIface.SpringSetChainLeft1.b_DeEnergized | 1 | 10.168.100.32 | Spring set chain left 1 | The spring set has detected a problem at the chain.
70 | ALN1 | 11201017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 70 | [DFR031]SFT_DA_LimitSwitch_ErrIface.SpringSetChainRight1.b_DeEnergized | 1 | 10.168.100.32 | Spring set chain right 1 | The spring set has detected a problem at the chain.
71 | ALN1 | 11201018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed. |  |  |  | 71 | [DFR031]SFT_DA_LimitSwitch_ErrIface.SpringSetChainLeft2.b_DeEnergized | 1 | 10.168.100.32 | Spring set chain left 2 | The spring set has detected a problem at the chain.
72 | ALN2/SM | 12010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 72 | [DFR031]SFT_DA_LimitSwitch_ErrIface.SpringSetChainRight2.b_DeEnergized | 1 | 10.168.100.32 | Spring set chain right 2 | The spring set has detected a problem at the chain.
73 | ALN2/SM | 12010001 | Service mode active | The aligner is in service mode. No aligning possible. |  |  |  | 73 | [DFR031]DA_Ctr_ErrIface.b_AccuEmpty | 1 | 10.168.100.32 | Buffer empty | There are no products in the buffer any more. It is empty.
74 | ALN2/SM | 12010002 | Calculation active | The unit is in calculation state. |  |  |  | 74 | [DFR031]DAI_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
75 | ALN2/SM | 12010003 | Switched off | The aligner is disabled. |  |  |  | 75 | [DFR031]DAI_SM_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | The infeed of the buffer is in service mode. No production active.
76 | ALN2/SM | 12010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 76 | [DFR031]DAI_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
77 | ALN2/Saf | 12020010 | cover open | There is a guard on the machine which is open. |  |  |  | 77 | [DFR031]DAI_SM_ErrIface.b_StateMachineDisabled | 1 | 10.168.100.32 | Unit switched off | The unit is disabled.
78 | ALN2/Saf | 12020018 | cover open requested | The guard will be open if the last move is done. |  |  |  | 78 | [DFR031]DAI_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
79 | ALN2/Saf | 12020060 | Energize drive fault | The energizing of the drive is faulted. |  |  |  | 79 | [DFR031]DAI_SM_ErrIface.b_Deactivated | 1 | 10.168.100.32 | Deactivated | The infeed is deactivated. No rows will be taken over by the infeed.
80 | ALN2/Saf | 12020090 | Exhaust valve fault | The exhaust valve has a fault. |  |  |  | 80 | [DFR031]SFT_DAI_Saf_ErrIface.CoverLeftBottom.b_DeEnergized | 1 | 10.168.100.32 | Door open left
81 | ALN2/Saf | 12020091 | Restarting exhaust valve | The exhaust valve is restarting. |  |  |  | 81 | [DFR031]SFT_DAI_Saf_ErrIface.CoverRightBottom.b_DeEnergized | 1 | 10.168.100.32 | Door open right
82 | ALN2/Saf | 12020092 | Energize exhaust valve fault | The energizing of the valve is faulted. |  |  |  | 82 | [DFR031]DAI_Saf_ErrIface.b_CoverOpenRequestedBottom | 1 | 10.168.100.32 | Doors open requested | The door will be unlocked if the last move is done.
83 | ALN2/Saf | 12020093 | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 83 | [DFR031]SFT_DAI_Saf_ErrIface.CoverLeftTop.b_DeEnergized | 1 | 10.168.100.32 | Door open left
84 | ALN2/Saf | 12020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system. |  |  |  | 84 | [DFR031]SFT_DAI_Saf_ErrIface.CoverRightTop.b_DeEnergized | 1 | 10.168.100.32 | Door open right
85 | ALN2 | 12200000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 85 | [DFR031]DAI_Saf_ErrIface.b_CoverOpenRequestedTop | 1 | 10.168.100.32 | Doors open requested | The door will be unlocked if the last move is done.
86 | ALN2 | 12200001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 86 | [DFR031]SFT_DAI_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
87 | ALN2 | 12200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 87 | [DFR031]DAI_Saf_ErrIface.b_ExhaustValveFault | 1 | 10.168.100.32 | Exhaust valve fault | The exhaust valve has a fault.
88 | ALN2 | 12200003 | Validation error | This is a validation error. One of the values is out of range. |  |  |  | 88 | [DFR031]DAI_Saf_ErrIface.b_RestartingExhaustValve | 1 | 10.168.100.32 | Restarting exhaust valve | The exhaust valve is restarting.
89 | ALN2 | 12200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 89 | [DFR031]SFT_DAI_Saf_ErrIface.EnergizeExhaustValve.b_DeEnergized | 1 | 10.168.100.32 | Energize exhaust valve fault | The energizing of the valve is faulted.
90 | ALN2 | 12200006 | Homing not possible | The motors of the aligner cannot be synchronized in the set time limit. |  |  |  | 90 | [DFR031]DAI_Saf_ErrIface.b_NoCompAir | 1 | 10.168.100.32 | Air pressure too low | The air pressure is below the allowed operating level.
91 | ALN2 | 12200010 | Acc / Dec out of range | This is a validation error. Acceleration / deceleration out of range (bigger than maximum, or less than the minimum required to decelerate after aligning into the open position). |  |  |  | 91 | [DFR031]DAI_Saf_ErrIface.b_CompAirNotExhaust | 1 | 10.168.100.32 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
92 | ALN2 | 12200011 | Cycle time of the aligner too long | This is a validation error. The aligner needs too long for a cycle. Increase speeds and acc/dec to speed-up the aligner. |  |  |  | 92 | [DFR031]DAI_Ctr_ErrIface.b_JamAtInfeedMsg | 1 | 10.168.100.32 | Jam at infeed | There is a product jam at the infeed of the buffer.
93 | ALN2 | 12200012 | Wrong aligner distance | This is a validation error. The aligner is too close to its start position. |  |  |  | 93 | [DFR031]DAI_Ctr_ErrIface.b_JamAtInfeedErr | 1 | 10.168.100.32 | Jam at infeed | There is a product jam at the infeed of the buffer.
94 | ALN2 | 12200013 | End move is too fast | This is a validation error. If the option clever aligning is on we have to move into the gap directly - without waiting in the open position. If the last move is too fast we would touch the rear edge of the row. |  |  |  | 94 | [DFR031]DAI_Ctr_ErrIface.b_CheckPhotoeyeInf | 1 | 10.168.100.32 | Infeed sensor not ready | The sensor on the belt right at the infeed of the buffer has been covered for a too long time.
95 | ALN2 | 12200014 | Adjustment error | This is an adjustment error. One of the values is out of range. |  |  |  | 95 | [DFR031]DAI_Ctr_ErrIface.b_MaxWorkingLevel | 1 | 10.168.100.32 | Maximum working level active | Infeed will start again if filling level is below a certain limit.
96 | ALN2 | 12200016 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 96 | [DFR031]DAI_Ctr_ErrIface.b_ShuttleAtBottomInit | 1 | 10.168.100.32 | Shuttle at bottom proximity switch | If the shuttle is at the bottom proximity switch, the infeed is blocked. It will not start moving again before the proximity switch is not activated any more and the maximum level for re-starting the infeed has been reached (hysteresis).
97 | ALN2 | 12200017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 97 | [DFR031]DAI_Ctr_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
98 | ALN2 | 12200018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed. |  |  |  | 98 | [DFR031]DAI_Ctr_ErrIface.b_HabShuttleAtInitHab | 1 | 10.168.100.32 | HAB shuttle at HAB drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the HAB drive is running forward.
99 | ALN2 | 12200019 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 99 | [DFR031]DAI_Ctr_ErrIface.b_HabShuttleAtInitChain | 1 | 10.168.100.32 | HAB shuttle at main chain drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the main chain drive is running forward.
100 | ALN2 | 12200020 | Home needed | The aligner is stopping to home after restart. |  |  |  | 100 | [DFR031]DAI_Ctr_ErrIface.b_CircuitBreakIonizationDevice | 1 | 10.168.100.32 | Circuit breaker ionization device | The circuit breaker is switched off.
101 | ALN2 | 12200021 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast. |  |  |  | 101 | [DFR031]DAI_Ctr_ErrIface.b_WaitForDischargeToEmpty | 1 | 10.168.100.32 | Not displayed on HMI!
102 | ALN2 | 12200022 | Product too high | There is a too high product detected in front of the aligner. |  |  |  | 102 | [DFR031]DAI_AxChain_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
103 | ALN2 | 12201004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 103 | [DFR031]DAI_AxChain_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
104 | ALN2 | 12201016 | Warning photoeye is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 104 | [DFR031]DAI_AxChain_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
105 | ALN2 | 12201017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 105 | [DFR031]DAI_AxChain_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
106 | ALN2 | 12201018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed. |  |  |  | 106 | [DFR031]DAI_AxChain_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
107 | DBP/SM | 15010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 107 | [DFR031]DAI_AxChain_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
108 | DBP/SM | 15010001 | Service mode active | The unit is in service mode. No production active. |  |  |  | 108 | [DFR031]DAI_AxChain_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
109 | DBP/SM | 15010002 | Calculation active | The unit is in calculation state. |  |  |  | 109 | [DFR031]DAI_AxChain_ErrIface.b_ProxNotFound | 1 | 10.168.100.32 | Home sensor error | The home sensor has not detected any gondola during normal run.
110 | DBP/SM | 15010003 | Unit switched off | The unit is disabled. |  |  |  | 110 | [DFR031]DAI_AxFsu_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
111 | DBP/SM | 15010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 111 | [DFR031]DAI_AxFsu_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
112 | DBP | 15200000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 112 | [DFR031]DAI_AxFsu_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
113 | DBP | 15200001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 113 | [DFR031]DAI_AxFsu_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
114 | DBP | 15200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 114 | [DFR031]DAI_AxFsu_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
115 | DBP | 15200003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 115 | [DFR031]DAI_AxFsu_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
116 | DBP | 15200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 116 | [DFR031]DAI_AxFsu_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
117 | DBP | 15200006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 117 | [DFR031]DAI_AxHab_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
118 | DBP | 15200010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 118 | [DFR031]DAI_AxHab_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
119 | DBP | 15200011 | Negative overtravel | The axis has exceeded the software limit position in negative direction. |  |  |  | 119 | [DFR031]DAI_AxHab_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
120 | DBP | 15200012 | Positive overtravel | The axis has exceeded the software limit position in positive direction. |  |  |  | 120 | [DFR031]DAI_AxHab_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
121 | DBP | 15200014 | Adjustment error | This is an adjustment error. One of the values is out of range. |  |  |  | 121 | [DFR031]DAI_AxHab_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
122 | DBP | 15200017 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...). |  |  |  | 122 | [DFR031]DAI_AxHab_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
123 | DBP | 15200018 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed. |  |  |  | 123 | [DFR031]DAI_AxHab_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
124 | BLTHOL/SM | 17010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 124 | [DFR031]DAI_AxHab_ErrIface.b_WrongSpd | 1 | 10.168.100.32 | Wrong speed | This is a validation error. A speed or the proportional factor to calculate the speed are incorrect.
125 | BLTHOL/SM | 17010001 | Service mode active | The process belts are in service mode. No production possible |  |  |  | 125 | [DFR031]DAI_LimitSwitch_ErrIface.b_HabShuttleChainEndSwitchMuted | 1 | 10.168.100.32 | Infeed HAB shuttle at main drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the main chain drive is running forward. The limit switch will be muted for a short time only.
126 | BLTHOL/SM | 17010002 | Calculation active | The unit is in calculation state. |  |  |  | 126 | [DFR031]DAI_LimitSwitch_ErrIface.b_HabShuttleHabEndSwitchMuted | 1 | 10.168.100.32 | Infeed HAB shuttle at HAB drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the HAB drive is running forward. The limit switch will be muted for a short time only.
127 | BLTHOL/SM | 17010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 127 | [DFR031]SFT_DAI_LimitSwitch_ErrIface.HabShuttleChainEndSwitch.b_DeEnergized | 1 | 10.168.100.32 | Infeed HAB shuttle at main drive limit switch | The HAB shuttle is at the limit switch which is activated if the main chain drive is running forward.
128 | BLTHOL/SM | 17010005 | Clean mode belts active | The process belts are in clean mode. No production possible. |  |  |  | 128 | [DFR031]SFT_DAI_LimitSwitch_ErrIface.HabShuttleHabEndSwitch.b_DeEnergized | 1 | 10.168.100.32 | Infeed HAB shuttle at HAB drive limit switch | The HAB shuttle is at the limit switch which is activated if the HAB drive is running forward.
129 | BLTHOL/SM | 17010006 | Empty mode belts is active | The belt empty mode is active. |  |  |  | 129 | [DFR031]DAI_LimitSwitch_ErrIface.b_PreventJogChain | 1 | 10.168.100.32 | Not displayed on HMI! | (Prevent Jog Chain)
130 | BLTHOL/Saf | 17020060 | Energize drives fault Rack 1 | The energizing of the drive is faulted. |  |  |  | 130 | [DFR031]DAI_LimitSwitch_ErrIface.b_PreventJogHab | 1 | 10.168.100.32 | Not displayed on HMI! | (Prevent Jog HAB)
131 | BLTHOL/Saf | 17020061 | Energize drives fault Rack 2 | The energizing of the drive is faulted. |  |  |  | 131 | [DFR031]DAI_RowDet_ErrIface.b_RowSim | 1 | 10.168.100.32 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
132 | BLTHOL/Saf | 17020065 | Energize drives fault belt track | The energizing of the belt track drive is faulted. |  |  |  | 132 | [DFR031]DAD_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
133 | BLTHOL/Saf | 17020090 | Exhaust valve fault | The exhaust valve has a fault. |  |  |  | 133 | [DFR031]DAD_SM_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | The discharge of the buffer is in service mode. No production active.
134 | BLTHOL/Saf | 17020091 | Restarting exhaust valve | The exhaust valve is restarting. |  |  |  | 134 | [DFR031]DAD_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
135 | BLTHOL/Saf | 17020092 | Energize exhaust valve fault | The energizing of the valve is faulted. |  |  |  | 135 | [DFR031]DAD_SM_ErrIface.b_StateMachineDisabled | 1 | 10.168.100.32 | Unit switched off | The unit is disabled.
136 | BLTHOL/Saf | 17020093 | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 136 | [DFR031]DAD_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
137 | BLTHOL/Saf | 17020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system. |  |  |  | 137 | [DFR031]DAD_SM_ErrIface.b_Deactivated | 1 | 10.168.100.32 | Deactivated | The discharge is deactivated. No rows will be discharged.
138 | BLTHOL_U1Left/Saf | 17022060 | Energize drives fault | The energizing of the drive is faulted. |  |  |  | 138 | [DFR031]SFT_DAD_Saf_ErrIface.CoverLeftBottom.b_DeEnergized | 1 | 10.168.100.32 | Door open left
139 | BLTHOL_U2Left/Saf | 17022064 | Not In working position | The belt is not in down position, therefore it is not possible to run the belt. |  |  |  | 139 | [DFR031]SFT_DAD_Saf_ErrIface.CoverRightBottom.b_DeEnergized | 1 | 10.168.100.32 | Door open right
140 | BLTHOL_U1Right/Saf | 17023060 | Energize drives fault | The energizing of the drive is faulted. |  |  |  | 140 | [DFR031]SFT_DAD_Saf_ErrIface.CoverMute.b_DeEnergized | 1 | 10.168.100.32 | Muting fault | Cleaning mute failed.
141 | BLTHOL_U2Right/Saf | 17023064 | Not In working position | The belt is not in down position, therefore it is not possible to run the belt. |  |  |  | 141 | [DFR031]DAD_Saf_ErrIface.b_CoverOpenRequestedBottom | 1 | 10.168.100.32 | Doors open requested | The door will be unlocked if the last move is done.
142 | BLTHOL/Ctr | 17100000 | Downstream equipment not ready | The downstream equipment is not ready. |  |  |  | 142 | [DFR031]SFT_DAD_Saf_ErrIface.CoverLeftTop.b_DeEnergized | 1 | 10.168.100.32 | Door open left
143 | BLTHOL/Ctr | 17100001 | Empty belts active until DDU1 | Upstream is not ready. No product is coming in from upstream. |  |  |  | 143 | [DFR031]SFT_DAD_Saf_ErrIface.CoverRightTop.b_DeEnergized | 1 | 10.168.100.32 | Door open right
144 | BLTHOL/Ctr | 17100999 | Not displayed on HMI! |  |  |  |  | 144 | [DFR031]DAD_Saf_ErrIface.b_CoverOpenRequestedTop | 1 | 10.168.100.32 | Doors open requested | The door will be unlocked if the last move is done.
145 | RR1 | 17105000 | Drive fault | There is a fault on this drive. |  |  |  | 145 | [DFR031]SFT_DAD_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
146 | RR1 | 17105001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 146 | [DFR031]DAD_Saf_ErrIface.b_ExhaustValveFault | 1 | 10.168.100.32 | Exhaust valve fault | The exhaust valve has a fault.
147 | RR1 | 17105002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 147 | [DFR031]DAD_Saf_ErrIface.b_RestartingExhaustValve | 1 | 10.168.100.32 | Restarting exhaust valve | The exhaust valve is restarting.
148 | RR1 | 17105003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 148 | [DFR031]SFT_DAD_Saf_ErrIface.EnergizeExhaustValve.b_DeEnergized | 1 | 10.168.100.32 | Energize exhaust valve fault | The energizing of the valve is faulted.
149 | RR1 | 17105004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 149 | [DFR031]DAD_Saf_ErrIface.b_NoCompAir | 1 | 10.168.100.32 | Air pressure too low | The air pressure is below the allowed operating level.
150 | RR1 | 17105010 | Photoeye row detection is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this. |  |  |  | 150 | [DFR031]DAD_Saf_ErrIface.b_CompAirNotExhaust | 1 | 10.168.100.32 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
151 | RR1 | 17105011 | Adjustment fault | There is a functional fault. It is not possible to do the commanded function of the row regulation belt due to bad parameter settings. |  |  |  | 151 | [DFR031]DAD_DIface_ErrIface.b_SetpointSim | 1 | 10.168.100.32 | Setpoint simulation active | Setpoint simulation at discharge of buffer is switched on.
152 | RR1/Track | 17107000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 152 | [DFR031]DAD_DIface_ErrIface.b_WrongFillLevelForSetpoint | 1 | 10.168.100.32 | Wrong fill level for setpoint | The proportion of parameters for calculating the setpoint to the downstream machine are not correct.
153 | RR1/Track | 17107001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 153 | [DFR031]DAD_DIface_ErrIface.b_DischargeNotReady1 | 1 | 10.168.100.32 | Discharge 1 not ready | The corresponding distribution leg is not ready.
154 | RR1/Track | 17107002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt. |  |  |  | 154 | [DFR031]DAD_DIface_ErrIface.b_CommFaultWithLeg1 | 1 | 10.168.100.32 | Ethernet communication fault with leg 1 | An ethernet fault with the packaging leg is active.
155 | RR1/Track | 17107003 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked. |  |  |  | 155 | [DFR031]DAD_DIface_ErrIface.b_DifaceDisabled1 | 1 | 10.168.100.32 | Discharge 1 disabled | The downstream interface is disabled.
156 | RR2 | 17110000 | Drive fault | There is a fault on this drive. |  |  |  | 156 | [DFR031]DAD_DIface_ErrIface.b_McSim1 | 1 | 10.168.100.32 | Mc simulation discharge 1 active | Machine simulation at discharge of buffer is switched on.
157 | RR2 | 17110001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 157 | [DFR031]DAD_DIface_ErrIface.b_DischargeNotReady2 | 1 | 10.168.100.32 | Discharge 2 not ready | The corresponding distribution leg is not ready.
158 | RR2 | 17110002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 158 | [DFR031]DAD_DIface_ErrIface.b_CommFaultWithLeg2 | 1 | 10.168.100.32 | Ethernet communication fault with leg 2 | An ethernet fault with the packaging leg is active.
159 | RR2 | 17110003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 159 | [DFR031]DAD_DIface_ErrIface.b_DifaceDisabled2 | 1 | 10.168.100.32 | Discharge 2 disabled | The downstream interface is disabled.
160 | RR2 | 17110004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 160 | [DFR031]DAD_DIface_ErrIface.b_McSim2 | 1 | 10.168.100.32 | Mc simulation discharge 2 active | Machine simulation at discharge of buffer is switched on.
161 | RR2 | 17110010 | Photoeye row detection is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this. |  |  |  | 161 | [DFR031]DAD_Ctr_ErrIface.b_ShelfNotInPos1 | 1 | 10.168.100.32 | Sensor shelf in pos at pusher 1 not ready | The sensor shelf in position at the pusher of the discharge is not working properly or is either dirty or misadjusted or the gondola is either not mounted properly or has stopped at a wrong position.
162 | RR2 | 17110011 | Adjustment fault | There is a functional fault. It is not possible to do the commanded function of the row regulation belt due to bad parameter settings. |  |  |  | 162 | [DFR031]DAD_Ctr_ErrIface.b_ShelfNotInPos2 | 1 | 10.168.100.32 | Sensor shelf in pos at pusher 2 not ready | The sensor shelf in position at the pusher of the discharge is not working properly or is either dirty or misadjusted or the gondola is either not mounted properly or has stopped at a wrong position.
163 | RR2/Track | 17112000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 163 | [DFR031]DAD_Ctr_ErrIface.b_MoveDistTooBig | 1 | 10.168.100.32 | Wrong move distance calculated | The cotroller calculated a move distance which is too big.
164 | RR2/Track | 17112001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 164 | [DFR031]DAD_Ctr_ErrIface.b_MinWorkingLevel | 1 | 10.168.100.32 | Minimum working level active | Discharge will start again if filling level is above a certain limit.
165 | RR2/Track | 17112002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt. |  |  |  | 165 | [DFR031]DAD_Ctr_ErrIface.b_ShuttleAtTopInit | 1 | 10.168.100.32 | Shuttle at top proximity switch | If the shuttle is at the top proximity switch, the discharge is blocked. It will not start moving again before the proximity switch is not activated any more and the minimum level for re-starting the discharge has been reached (hysteresis).
166 | RR2/Track | 17112003 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked. |  |  |  | 166 | [DFR031]DAD_Ctr_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
167 | BLTHOL/U1 | 17200000 | Drive fault | There is a fault on this drive. |  |  |  | 167 | [DFR031]DAD_Ctr_ErrIface.b_WrongStabilizTime1 | 1 | 10.168.100.32 | Wrong stabilization time pusher 1 | The product parameter for row stabilization time on the discharge belt is not in a valid range.
168 | BLTHOL/U1 | 17200001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 168 | [DFR031]DAD_Ctr_ErrIface.b_WrongStabilizTime2 | 1 | 10.168.100.32 | Wrong stabilization time pusher 2 | The product parameter for row stabilization time on the discharge belt is not in a valid range.
169 | BLTHOL/U1 | 17200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 169 | [DFR031]DAD_Ctr_ErrIface.b_DischBlt1NotInWorkingPos | 1 | 10.168.100.32 | Discharge belt 1 not in working position | Move the discharge belt toward the buffer and lock it.
170 | BLTHOL/U1 | 17200003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 170 | [DFR031]DAD_Ctr_ErrIface.b_DischBlt2NotInWorkingPos | 1 | 10.168.100.32 | Discharge belt 2 not in working position | Move the discharge belt toward the buffer and lock it.
171 | BLTHOL/U1 | 17200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 171 | [DFR031]DAD_Ctr_ErrIface.b_HabShuttleAtInitHab | 1 | 10.168.100.32 | HAB shuttle at HAB drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the HAB drive is running forward.
172 | BLTHOL/U1 | 17200012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 172 | [DFR031]DAD_Ctr_ErrIface.b_HabShuttleAtInitChain | 1 | 10.168.100.32 | HAB shuttle at main drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the main chain drive is running forward.
173 | BLTHOL/U1 Track | 17201000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 173 | [DFR031]DAD_AxChain_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
174 | BLTHOL/U1 Track | 17201001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 174 | [DFR031]DAD_AxChain_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
175 | BLTHOL/U1 Track | 17201002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt. |  |  |  | 175 | [DFR031]DAD_AxChain_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
176 | BLTHOL/U1 Track | 17201003 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked. |  |  |  | 176 | [DFR031]DAD_AxChain_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
177 | BLTHOL/U1 Left | 17203000 | Drive fault | There is a fault on this drive. |  |  |  | 177 | [DFR031]DAD_AxChain_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
178 | BLTHOL/U1 Left | 17203001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 178 | [DFR031]DAD_AxChain_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
179 | BLTHOL/U1 Left | 17203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 179 | [DFR031]DAD_AxChain_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
180 | BLTHOL/U1 Left | 17203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 180 | [DFR031]DAD_AxChain_ErrIface.b_ProxNotFound | 1 | 10.168.100.32 | Home sensor error | The home sensor has not detected any gondola during normal run.
181 | BLTHOL/U1 Left | 17203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 181 | [DFR031]DAD_AxPush1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
182 | BLTHOL/U1 Left | 17203012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 182 | [DFR031]DAD_AxPush1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
183 | BLTHOL/U1 Right | 17204000 | Drive fault | There is a fault on this drive. |  |  |  | 183 | [DFR031]DAD_AxPush1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
184 | BLTHOL/U1 Right | 17204001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 184 | [DFR031]DAD_AxPush1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
185 | BLTHOL/U1 Right | 17204002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 185 | [DFR031]DAD_AxPush1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
186 | BLTHOL/U1 Right | 17204003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 186 | [DFR031]DAD_AxPush1_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
187 | BLTHOL/U1 Right | 17204004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 187 | [DFR031]DAD_AxPush1_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
188 | BLTHOL/U1 Right | 17204012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 188 | [DFR031]DAD_AxPush1_ErrIface.b_NeedSecurityPos | 1 | 10.168.100.32 | Not in working area | The pusher ist not in the working area. Chain and pusher moves are not possible.
189 | BLTHOL/U2 | 17210000 | Drive fault | There is a fault on this drive. |  |  |  | 189 | [DFR031]DAD_AxPush1_ErrIface.b_ProxNotFound | 1 | 10.168.100.32 | Home sensor error | The home sensor is not working properly.
190 | BLTHOL/U2 | 17210001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 190 | [DFR031]DAD_AxPush1_ErrIface.b_WrongPos | 1 | 10.168.100.32 | Wrong position | This is a validation error. Front or rear position are incorrect.
191 | BLTHOL/U2 | 17210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 191 | [DFR031]DAD_AxPush2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
192 | BLTHOL/U2 | 17210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 192 | [DFR031]DAD_AxPush2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
193 | BLTHOL/U2 | 17210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 193 | [DFR031]DAD_AxPush2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
194 | BLTHOL/U2 | 17210012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 194 | [DFR031]DAD_AxPush2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
195 | BLTHOL/U2 Track | 17211000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 195 | [DFR031]DAD_AxPush2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
196 | BLTHOL/U2 Track | 17211001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 196 | [DFR031]DAD_AxPush2_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
197 | BLTHOL/U2 Track | 17211002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt. |  |  |  | 197 | [DFR031]DAD_AxPush2_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
198 | BLTHOL/U2 Track | 17211003 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked. |  |  |  | 198 | [DFR031]DAD_AxPush2_ErrIface.b_NeedSecurityPos | 1 | 10.168.100.32 | Not in working area | The pusher ist not in the working area. Chain and pusher moves are not possible.
199 | BLTHOL/U3 | 17220000 | Drive fault | There is a fault on this drive. |  |  |  | 199 | [DFR031]DAD_AxPush2_ErrIface.b_ProxNotFound | 1 | 10.168.100.32 | Home sensor error | The home sensor is not working properly.
200 | BLTHOL/U3 | 17220001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 200 | [DFR031]DAD_AxPush2_ErrIface.b_WrongPos | 1 | 10.168.100.32 | Wrong position | This is a validation error. Front or rear position are incorrect.
201 | BLTHOL/U3 | 17220002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 201 | [DFR031]DAD_BackStop1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The device has been switched off.
202 | BLTHOL/U3 | 17220003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 202 | [DFR031]DAD_BackStop1_ErrIface.b_ProxNotFound | 1 | 10.168.100.32 | Proximity switch not found | The proximity limit switch of the device is not working correctly.
203 | BLTHOL/U3 | 17220004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 203 | [DFR031]DAD_BackStop2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The device has been switched off.
204 | BLTHOL/U3 | 17220012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 204 | [DFR031]DAD_BackStop2_ErrIface.b_ProxNotFound | 1 | 10.168.100.32 | Proximity switch not found | The proximity limit switch of the device is not working correctly.
205 | BLTHOL/U3 Track | 17221000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 205 | [DFR031]DAD_AxHab_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
206 | BLTHOL/U3 Track | 17221001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 206 | [DFR031]DAD_AxHab_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
207 | BLTHOL/U3 Track | 17221002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt. |  |  |  | 207 | [DFR031]DAD_AxHab_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
208 | BLTHOL/U3 Track | 17221003 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked. |  |  |  | 208 | [DFR031]DAD_AxHab_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
209 | BLTHOL/U4 | 17230000 | Drive fault | There is a fault on this drive. |  |  |  | 209 | [DFR031]DAD_AxHab_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
210 | BLTHOL/U4 | 17230001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 210 | [DFR031]DAD_AxHab_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
211 | BLTHOL/U4 | 17230002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 211 | [DFR031]DAD_AxHab_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
212 | BLTHOL/U4 | 17230003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 212 | [DFR031]DAD_AxHab_ErrIface.b_WrongSpd | 1 | 10.168.100.32 | Wrong speed | This is a validation error. A speed or the proportional factor to calculate the speed are incorrect.
213 | BLTHOL/U4 | 17230004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 213 | [DFR031]DAD_LimitSwitch_ErrIface.b_HabShuttleChainEndSwitchMuted | 1 | 10.168.100.32 | Discharge HAB shuttle at main drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the main chain drive is running forward. The limit switch will be muted for a short time only.
214 | BLTHOL/U4 | 17230012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 214 | [DFR031]DAD_LimitSwitch_ErrIface.b_HabShuttleHabEndSwitchMuted | 1 | 10.168.100.32 | Discharge HAB shuttle at HAB drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the HAB drive is running forward. The limit switch will be muted for a short time only.
215 | BLTHOL/U4 Track | 17231000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 215 | [DFR031]SFT_DAD_LimitSwitch_ErrIface.HabShuttleChainEndSwitch.b_DeEnergized | 1 | 10.168.100.32 | Discharge HAB shuttle at main drive limit switch | The HAB shuttle at discharge is at the limit switch which is activated if the main chain drive is running forward.
216 | BLTHOL/U4 Track | 17231001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 216 | [DFR031]SFT_DAD_LimitSwitch_ErrIface.HabShuttleHabEndSwitch.b_DeEnergized | 1 | 10.168.100.32 | Discharge HAB shuttle at HAB drive limit switch | The HAB shuttle at discharge is at the limit switch which is activated if the HAB drive is running forward.
217 | BLTHOL/U4 Track | 17231002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt. |  |  |  | 217 | [DFR031]DAD_LimitSwitch_ErrIface.b_PreventJogChain | 1 | 10.168.100.32 | Not displayed on HMI! | (Prevent Jog Chain)
218 | BLTHOL/U4 Track | 17231003 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked. |  |  |  | 218 | [DFR031]DAD_LimitSwitch_ErrIface.b_PreventJogHab | 1 | 10.168.100.32 | Not displayed on HMI! | (Prevent Jog HAB)
219 | BLTHOL/DDU1 | 17400000 | Drive fault | There is a fault on this drive. |  |  |  | 219 | [DFR031]DAI_Tilting_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The device has been switched off.
220 | BLTHOL/DDU1 | 17400001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 220 | [DFR031]DAI_Tilting_ErrIface.b_NeedSecurityPos | 1 | 10.168.100.32 | Not in working area | The device is not in the working area. Chain moves are not possible.
221 | BLTHOL/DDU1 | 17400002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 221 | [DFR031]DAI_Tilting_ErrIface.b_ProxNotFound | 1 | 10.168.100.32 | Proximity switch not found | The proximity limit switch of the device is not working correctly.
222 | BLTHOL/DDU1 | 17400003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 222 | [DFR031]GAPCLO1_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
223 | BLTHOL/DDU1 | 17400004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 223 | [DFR031]GAPCLO1_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
224 | BLTHOL/DDU1 | 17400012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 224 | [DFR031]SFT_GAPCLO1_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
225 | BLTHOL/DDU1 Track | 17401000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 225 | [DFR031]SFT_GAPCLO1_Saf_ErrIface.EnergizeDischBeltLowDrive.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault lower discharge belt | The energizing of the drive is faulted.
226 | BLTHOL/DDU1 Track | 17401001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 226 | [DFR031]GAPCLO1_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
227 | BLTHOL/DDU1 Track | 17401002 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt. |  |  |  | 227 | [DFR031]GAPCLO1_Ctr_ErrIface.b_JamAtDischargeBelt | 1 | 10.168.100.32 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
228 | BLTHOL/DDU1 Track | 17401003 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked. |  |  |  | 228 | [DFR031]GAPCLO1_Ctr_ErrIface.b_NeedHomeOrSynch | 1 | 10.168.100.32 | A part is not homed | The home procedure has not been carried out yet.
229 | BLTHOL/DDU1 Left | 17403000 | Drive fault | There is a fault on this drive. |  |  |  | 229 | [DFR031]GAPCLO1_Ctr_ErrIface.b_IsHomingOrSynch | 1 | 10.168.100.32 | Homing active | The feeding system is homing or synchronising
230 | BLTHOL/DDU1 Left | 17403001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 230 | [DFR031]H1_SMCtr_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
231 | BLTHOL/DDU1 Left | 17403002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 231 | [DFR031]H1_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
232 | BLTHOL/DDU1 Left | 17403003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 232 | [DFR031]GAPCLO1_AxDischBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
233 | BLTHOL/DDU1 Left | 17403004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 233 | [DFR031]GAPCLO1_AxDischBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
234 | BLTHOL/DDU1 Left | 17403012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 234 | [DFR031]GAPCLO1_AxDischBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
235 | BLTHOL/DDU1 Right | 17404000 | Drive fault | There is a fault on this drive. |  |  |  | 235 | [DFR031]GAPCLO1_AxDischBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
236 | BLTHOL/DDU1 Right | 17404001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 236 | [DFR031]GAPCLO1_AxDischBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
237 | BLTHOL/DDU1 Right | 17404002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 237 | [DFR031]GAPCLO1_AxDischBltUp_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
238 | BLTHOL/DDU1 Right | 17404003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 238 | [DFR031]GAPCLO1_AxDischBltUp_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
239 | BLTHOL/DDU1 Right | 17404004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 239 | [DFR031]GAPCLO1_AxDischBltUp_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
240 | BLTHOL/DDU1 Right | 17404012 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 240 | [DFR031]GAPCLO1_AxDischBltUp_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
241 | BLTHOL/DDU1 EvBlt | 17405000 | Drive fault | There is a fault on this drive. |  |  |  | 241 | [DFR031]GAPCLO1_AxDischBltUp_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
242 | BLTHOL/DDU1 EvBlt | 17405001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 242 | [DFR031]GAPCLO1_AxDischBltLow_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
243 | BLTHOL/DDU1 EvBlt | 17405002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 243 | [DFR031]GAPCLO1_AxDischBltLow_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
244 | BLTHOL/DDU1 EvBlt | 17405003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 244 | [DFR031]GAPCLO1_AxDischBltLow_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
245 | BLTHOL/DDU1 EvBlt | 17405004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 245 | [DFR031]GAPCLO1_AxDischBltLow_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
246 | BLTDAI/SM | 19010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 246 | [DFR031]GAPCLO1_AxDischBltLow_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
247 | BLTDAI/SM | 19010001 | Service mode active | The process belts are in service mode. No production possible |  |  |  | 247 | [DFR031]GAPCLO1_AxBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
248 | BLTDAI/SM | 19010002 | Calculation active | The unit is in calculation state. |  |  |  | 248 | [DFR031]GAPCLO1_AxBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
249 | BLTDAI/SM | 19010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 249 | [DFR031]GAPCLO1_AxBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
250 | BLTDAI/SM | 19010005 | Clean mode belts active | The process belts are in clean mode. No production possible. |  |  |  | 250 | [DFR031]GAPCLO1_AxBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
251 | BLTDAI/SM | 19010006 | Empty mode belts is active | The belt empty mode is active. |  |  |  | 251 | [DFR031]GAPCLO1_AxBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
252 | BLTDAI/Saf | 19020060 | Energize drives fault | The energizing of the drive is faulted. |  |  |  | 252 | [DFR031]GAPCLO1_AxBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
253 | BLTDAI/Saf | 19020090 | Exhaust valve fault | The exhaust valve has a fault. |  |  |  | 253 | [DFR031]GAPCLO1_AxBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
254 | BLTDAI/Saf | 19020091 | Restarting exhaust valve | The exhaust valve is restarting. |  |  |  | 254 | [DFR031]GAPCLO1_AxBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
255 | BLTDAI/Saf | 19020092 | Energize exhaust valve fault | The energizing of the valve is faulted. |  |  |  | 255 | [DFR031]GAPCLO1_AxBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
256 | BLTDAI/Saf | 19020093 | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 256 | [DFR031]GAPCLO1_AxBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
257 | BLTDAI/Saf | 19020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system. |  |  |  | 257 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
258 | BLTDAI/Belt | 19200000 | Drive fault | There is a fault on this drive. |  |  |  | 258 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
259 | BLTDAI/Belt | 19200001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 259 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
260 | BLTDAI/Belt | 19200002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 260 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
261 | BLTDAI/Belt | 19200003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 261 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
262 | BLTDAI/Belt | 19200004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 262 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
263 | BLTDAI/Belt | 19200010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 263 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
264 | BLTDAI/Belt | 19200012 | An element on belt is not ready | A unit on this belt is not ready, therefore it is not possible to run the belt in production. |  |  |  | 264 | [DFR031]GAPCLO1_AxDivr_ErrIface.b_PosNotValid | 1 | 10.168.100.32 | Invalid position parameter | The distance between up and down position is more than 180 degrees.
265 | BLTDAI/Belt track | 19201000 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 265 | [DFR031]GAPCLO2_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
266 | BLTDAI/Belt track | 19201001 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance. |  |  |  | 266 | [DFR031]GAPCLO2_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
267 | DDU1/SM | 41010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 267 | [DFR031]SFT_GAPCLO2_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
268 | DDU1/SM | 41010001 | Service mode active | The unit is in service mode. No production active. |  |  |  | 268 | [DFR031]SFT_GAPCLO2_Saf_ErrIface.EnergizeDischBeltLowDrive.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault lower discharge belt | The energizing of the drive is faulted.
269 | DDU1/SM | 41010002 | Calculation active | The unit is in calculation state. |  |  |  | 269 | [DFR031]GAPCLO2_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
270 | DDU1/SM | 41010003 | Unit switched off | The unit is disabled. |  |  |  | 270 | [DFR031]GAPCLO2_Ctr_ErrIface.b_JamAtDischargeBelt | 1 | 10.168.100.32 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
271 | DDU1/SM | 41010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 271 | [DFR031]GAPCLO2_Ctr_ErrIface.b_NeedHomeOrSynch | 1 | 10.168.100.32 | A part is not homed | The home procedure has not been carried out yet.
272 | DDU1/Saf | 41020010 | Door open left | There is a guard on the machine which is open. |  |  |  | 272 | [DFR031]GAPCLO2_Ctr_ErrIface.b_IsHomingOrSynch | 1 | 10.168.100.32 | Homing active | The feeding system is homing or synchronising
273 | DDU1/Saf | 41020011 | Door open right | There is a guard on the machine which is open. |  |  |  | 273 | [DFR031]H2_SMCtr_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
274 | DDU1/Saf | 41020018 | Doors open requested | The guard will be opened as soon as the last move is done. |  |  |  | 274 | [DFR031]H2_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
275 | DDU1/Saf | 41020060 | Energize drives fault | The energizing of the drive is faulted. |  |  |  | 275 | [DFR031]GAPCLO2_AxDischBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
276 | DDU1/Saf | 41020090 | Exhaust valve fault | The exhaust valve has a fault. |  |  |  | 276 | [DFR031]GAPCLO2_AxDischBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
277 | DDU1/Saf | 41020091 | Restarting exhaust valve | The exhaust valve is restarting. |  |  |  | 277 | [DFR031]GAPCLO2_AxDischBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
278 | DDU1/Saf | 41020092 | Energize exhaust valve fault | The energizing of the valve is faulted. |  |  |  | 278 | [DFR031]GAPCLO2_AxDischBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
279 | DDU1/Saf | 41020093 | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 279 | [DFR031]GAPCLO2_AxDischBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
280 | DDU1/Saf | 41020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system. |  |  |  | 280 | [DFR031]GAPCLO2_AxDischBltUp_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
281 | DDU1/Ctr | 41200001 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end. |  |  |  | 281 | [DFR031]GAPCLO2_AxDischBltUp_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
282 | DDU1/Ctr | 41200002 | Dump unit home needed | The dump unit is stopping to home after restart. |  |  |  | 282 | [DFR031]GAPCLO2_AxDischBltUp_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
283 | DDU1/Ctr | 41200003 | Manual dumping active | The manual dumping is active. |  |  |  | 283 | [DFR031]GAPCLO2_AxDischBltUp_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
284 | DDU1/Ctr | 41200004 | Remove all rows from diverter head | After emergency stop or fault, all products have to be removed from the diverter head. Opening and closing the guard of the unit when removing the products will automatically reset this message. |  |  |  | 284 | [DFR031]GAPCLO2_AxDischBltUp_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
285 | DDU1/Ctr | 41200005 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast. |  |  |  | 285 | [DFR031]GAPCLO2_AxDischBltLow_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
286 | DDU1/Ctr | 41200011 | Vision camera not ready | Vision camera is not ready. |  |  |  | 286 | [DFR031]GAPCLO2_AxDischBltLow_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
287 | DDU1/Ctr | 41200012 | Data transfer active | Data is being sent to the controller. This message will disappear automatically. |  |  |  | 287 | [DFR031]GAPCLO2_AxDischBltLow_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
288 | DDU1/Ctr | 41200014 | Too many rows in register | There are too many rows between the photoeye and the move position of the diverter. |  |  |  | 288 | [DFR031]GAPCLO2_AxDischBltLow_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
289 | DDU1/Ctr | 41200014 | Too many rows in register | There are too many rows between the photoeye and the move position of the pullnose. |  |  |  | 289 | [DFR031]GAPCLO2_AxDischBltLow_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
290 | DDU1/Ctr | 41200015 | Photoeye row detection not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this. |  |  |  | 290 | [DFR031]GAPCLO2_AxBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
291 | DDU1/Ctr | 41200016 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this. |  |  |  | 291 | [DFR031]GAPCLO2_AxBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
292 | DDU1/Ctr | 41200017 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed. |  |  |  | 292 | [DFR031]GAPCLO2_AxBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
293 | DDU1/Ctr | 41200020 | Diverter invalid position parameter | The distance between the dump- and the pass position is more than 180 degrees. |  |  |  | 293 | [DFR031]GAPCLO2_AxBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
294 | DDU1/Ctr | 41200030 | Pullnose invalid position parameter | The distance between the open- and the close position is more than 180 degrees. |  |  |  | 294 | [DFR031]GAPCLO2_AxBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
295 | DDU1/Ctr | 41200031 | Pullnose open speed profile not valid | Acceleration and deceleration to open the pullnose are too low or the speed is less than the speed of the belt. |  |  |  | 295 | [DFR031]GAPCLO2_AxBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
296 | DDU1/Ctr | 41200032 | Pullnose close speed profile not valid | Parameter for maximum speed or calculated speed to close the pullnose is less than the belt speed or the calculated deceleration is too high. |  |  |  | 296 | [DFR031]GAPCLO2_AxBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
297 | DDU1/Ctr | 41200050 | Metaldetector not ready | The metaldetector which is usually required to operate the system under normal circumstances is not ready (initalization active, faulty or turned off locally). |  |  |  | 297 | [DFR031]GAPCLO2_AxBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
298 | DDU1/Ctr | 41200051 | Metaldetector overload | Overload metaldetector. |  |  |  | 298 | [DFR031]GAPCLO2_AxBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
299 | DDU1/Diverter | 41203000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 299 | [DFR031]GAPCLO2_AxBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
300 | DDU1/Diverter | 41203001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 300 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
301 | DDU1/Diverter | 41203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 301 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
302 | DDU1/Diverter | 41203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 302 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
303 | DDU1/Diverter | 41203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 303 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
304 | DDU1/Diverter | 41203006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 304 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
305 | DDU1/Diverter | 41203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 305 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
306 | DDU1/Pullnose | 41204000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 306 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
307 | DDU1/Pullnose | 41204001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 307 | [DFR031]GAPCLO2_AxDivr_ErrIface.b_PosNotValid | 1 | 10.168.100.32 | Invalid position parameter | The distance between up and down position is more than 180 degrees.
308 | DDU1/Pullnose | 41204002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 308 | [DFR031]GAPCLO3_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
309 | DDU1/Pullnose | 41204003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 309 | [DFR031]GAPCLO3_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
310 | DDU1/Pullnose | 41204004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 310 | [DFR031]SFT_GAPCLO3_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
311 | DDU1/Pullnose | 41204006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 311 | [DFR031]GAPCLO3_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
312 | DDU1/Pullnose | 41204010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 312 | [DFR031]GAPCLO3_Ctr_ErrIface.b_JamAtDischargeBelt | 1 | 10.168.100.32 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
313 | DA/SMCtr | 44009000 | Mode empty active |  |  |  |  | 313 | [DFR031]GAPCLO3_Ctr_ErrIface.b_NeedHomeOrSynch | 1 | 10.168.100.32 | A part is not homed | The home procedure has not been carried out yet.
314 | DA/SMCtr | 44009001 | Mode clean active |  |  |  |  | 314 | [DFR031]GAPCLO3_Ctr_ErrIface.b_IsHomingOrSynch | 1 | 10.168.100.32 | Homing active | The feeding system is homing or synchronising
315 | DA/SMCtr | 44009002 | Mode fill active |  |  |  |  | 315 | [DFR031]H3_SMCtr_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
316 | DA/Ctr | 44200001 | Buffer empty | There are no products in the buffer any more. It is empty. |  |  |  | 316 | [DFR031]H3_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
317 | Limit Switch | 44231000 | Shuttle at top limit switch muted | The Shuttle is at the top limit switch and muted. |  |  |  | 317 | [DFR031]GAPCLO3_AxDischBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
318 | Limit Switch | 44231001 | Shuttle at bottom limit switch muted | The Shuttle is at the bottom limit switch and muted. |  |  |  | 318 | [DFR031]GAPCLO3_AxDischBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
319 | Limit Switch | 44231010 | Shuttle at top limit switch | The Shuttle is at the top limit switch. |  |  |  | 319 | [DFR031]GAPCLO3_AxDischBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
320 | Limit Switch | 44231011 | Shuttle at bottom limit switch | The Shuttle is at the bottom limit switch. |  |  |  | 320 | [DFR031]GAPCLO3_AxDischBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
321 | Limit Switch | 44231021 | Spring set chain left 1 | The spring set has detected a problem at the chain. |  |  |  | 321 | [DFR031]GAPCLO3_AxDischBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
322 | Limit Switch | 44231022 | Spring set chain right 1 | The spring set has detected a problem at the chain. |  |  |  | 322 | [DFR031]GAPCLO3_AxBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
323 | Limit Switch | 44231023 | Spring set chain left 2 | The spring set has detected a problem at the chain. |  |  |  | 323 | [DFR031]GAPCLO3_AxBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
324 | Limit Switch | 44231024 | Spring set chain right 2 | The spring set has detected a problem at the chain. |  |  |  | 324 | [DFR031]GAPCLO3_AxBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
325 | DAI/SM | 45010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 325 | [DFR031]GAPCLO3_AxBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
326 | DAI/SM | 45010001 | Service mode active | The infeed of the buffer is in service mode. No production active. |  |  |  | 326 | [DFR031]GAPCLO3_AxBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
327 | DAI/SM | 45010002 | Calculation active | The unit is in calculation state. |  |  |  | 327 | [DFR031]GAPCLO3_AxBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
328 | DAI/SM | 45010003 | Unit switched off | The unit is disabled. |  |  |  | 328 | [DFR031]GAPCLO3_AxBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
329 | DAI/SM | 45010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 329 | [DFR031]GAPCLO3_AxBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
330 | DAI/SM | 45010006 | Deactivated | The infeed is deactivated. No rows will be taken over by the infeed. |  |  |  | 330 | [DFR031]GAPCLO3_AxBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
331 | DAI/Saf/Bottom | 45020010 | Door open left |  |  |  |  | 331 | [DFR031]GAPCLO3_AxBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
332 | DAI/Saf/Bottom | 45020011 | Door open right |  |  |  |  | 332 | [DFR031]GAPCLO4_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
333 | DAI/Saf/Bottom | 45020018 | Doors open requested | The door will be unlocked if the last move is done. |  |  |  | 333 | [DFR031]GAPCLO4_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
334 | DAI/Saf/Top | 45020020 | Door open left |  |  |  |  | 334 | [DFR031]SFT_GAPCLO4_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
335 | DAI/Saf/Top | 45020021 | Door open right |  |  |  |  | 335 | [DFR031]GAPCLO4_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
336 | DAI/Saf/Top | 45020028 | Doors open requested | The door will be unlocked if the last move is done. |  |  |  | 336 | [DFR031]GAPCLO4_Ctr_ErrIface.b_JamAtDischargeBelt | 1 | 10.168.100.32 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
337 | DAI/Saf | 45020060 | Energize drives fault | The energizing of the drive is faulted. |  |  |  | 337 | [DFR031]GAPCLO4_Ctr_ErrIface.b_NeedHomeOrSynch | 1 | 10.168.100.32 | A part is not homed | The home procedure has not been carried out yet.
338 | DAI/Saf | 45020090 | Exhaust valve fault | The exhaust valve has a fault. |  |  |  | 338 | [DFR031]GAPCLO4_Ctr_ErrIface.b_IsHomingOrSynch | 1 | 10.168.100.32 | Homing active | The feeding system is homing or synchronising
339 | DAI/Saf | 45020091 | Restarting exhaust valve | The exhaust valve is restarting. |  |  |  | 339 | [DFR031]H4_SMCtr_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
340 | DAI/Saf | 45020092 | Energize exhaust valve fault | The energizing of the valve is faulted. |  |  |  | 340 | [DFR031]H4_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
341 | DAI/Saf | 45020093 | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 341 | [DFR031]GAPCLO4_AxDischBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
342 | DAI/Saf | 45020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system. |  |  |  | 342 | [DFR031]GAPCLO4_AxDischBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
343 | DAI/Ctr | 45200000 | Jam at infeed | There is a product jam at the infeed of the buffer. |  |  |  | 343 | [DFR031]GAPCLO4_AxDischBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
344 | DAI/Ctr | 45200001 | Jam at infeed | There is a product jam at the infeed of the buffer. |  |  |  | 344 | [DFR031]GAPCLO4_AxDischBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
345 | DAI/Ctr | 45200002 | Infeed sensor not ready | The sensor on the belt right at the infeed of the buffer has been covered for a too long time. |  |  |  | 345 | [DFR031]GAPCLO4_AxDischBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
346 | DAI/Ctr | 45200005 | Maximum working level active | Infeed will start again if filling level is below a certain limit. |  |  |  | 346 | [DFR031]GAPCLO4_AxBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
347 | DAI/Ctr | 45200007 | Shuttle at bottom proximity switch | If the shuttle is at the bottom proximity switch, the infeed is blocked. It will not start moving again before the proximity switch is not activated any more and the maximum level for re-starting the infeed has been reached (hysteresis). |  |  |  | 347 | [DFR031]GAPCLO4_AxBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
348 | DAI/Ctr | 45200010 | Validation fault | The module detected a value out of range. |  |  |  | 348 | [DFR031]GAPCLO4_AxBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
349 | DAI/Ctr | 45200020 | HAB shuttle at HAB drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the HAB drive is running forward. |  |  |  | 349 | [DFR031]GAPCLO4_AxBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
350 | DAI/Ctr | 45200021 | HAB shuttle at main chain drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the main chain drive is running forward. |  |  |  | 350 | [DFR031]GAPCLO4_AxBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
351 | DAI/Ctr | 45200030 | Circuit breaker ionization device | The circuit breaker is switched off. |  |  |  | 351 | [DFR031]GAPCLO4_AxBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
352 | DAI/Ctr | 45200999 | Not displayed on HMI! |  |  |  |  | 352 | [DFR031]GAPCLO4_AxBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
353 | DAI/Chain | 45201000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 353 | [DFR031]GAPCLO4_AxBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
354 | DAI/Chain | 45201001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 354 | [DFR031]GAPCLO4_AxBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
355 | DAI/Chain | 45201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 355 | [DFR031]GAPCLO4_AxBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
356 | DAI/Chain | 45201003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 356 | [DFR031]GAPCLO5_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
357 | DAI/Chain | 45201004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 357 | [DFR031]GAPCLO5_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
358 | DAI/Chain | 45201006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 358 | [DFR031]SFT_GAPCLO5_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
359 | DAI/Chain | 45201010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 359 | [DFR031]GAPCLO5_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
360 | DAI/Chain | 45201012 | Home sensor error | The home sensor has not detected any gondola during normal run. |  |  |  | 360 | [DFR031]GAPCLO5_Ctr_ErrIface.b_JamAtDischargeBelt | 1 | 10.168.100.32 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
361 | DAI/HAB | 45202000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 361 | [DFR031]GAPCLO5_Ctr_ErrIface.b_NeedHomeOrSynch | 1 | 10.168.100.32 | A part is not homed | The home procedure has not been carried out yet.
362 | DAI/HAB | 45202001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 362 | [DFR031]GAPCLO5_Ctr_ErrIface.b_IsHomingOrSynch | 1 | 10.168.100.32 | Homing active | The feeding system is homing or synchronising
363 | DAI/HAB | 45202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 363 | [DFR031]H5_SMCtr_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
364 | DAI/HAB | 45202003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 364 | [DFR031]H5_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
365 | DAI/HAB | 45202004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 365 | [DFR031]GAPCLO5_AxDischBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
366 | DAI/HAB | 45202006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 366 | [DFR031]GAPCLO5_AxDischBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
367 | DAI/HAB | 45202010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 367 | [DFR031]GAPCLO5_AxDischBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
368 | DAI/HAB | 45202013 | Wrong speed | This is a validation error. A speed or the proportional factor to calculate the speed are incorrect. |  |  |  | 368 | [DFR031]GAPCLO5_AxDischBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
369 | DAI/FSU | 45203000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 369 | [DFR031]GAPCLO5_AxDischBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
370 | DAI/FSU | 45203001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 370 | [DFR031]GAPCLO5_AxBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
371 | DAI/FSU | 45203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 371 | [DFR031]GAPCLO5_AxBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
372 | DAI/FSU | 45203003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 372 | [DFR031]GAPCLO5_AxBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
373 | DAI/FSU | 45203004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 373 | [DFR031]GAPCLO5_AxBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
374 | DAI/FSU | 45203006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 374 | [DFR031]GAPCLO5_AxBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
375 | DAI/FSU | 45203010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 375 | [DFR031]GAPCLO5_AxBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
376 | DAI/Tilting Device | 45215004 | Switched off | The device has been switched off. |  |  |  | 376 | [DFR031]GAPCLO5_AxBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
377 | DAI/Tilting Device | 45215011 | Not in working area | The device is not in the working area. Chain moves are not possible. |  |  |  | 377 | [DFR031]GAPCLO5_AxBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
378 | DAI/Tilting Device | 45215012 | Proximity switch not found | The proximity limit switch of the device is not working correctly. |  |  |  | 378 | [DFR031]GAPCLO5_AxBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
379 | Limit Switch | 45231000 | Infeed HAB shuttle at main drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the main chain drive is running forward. The limit switch will be muted for a short time only. |  |  |  | 379 | [DFR031]GAPCLO5_AxBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
380 | Limit Switch | 45231001 | Infeed HAB shuttle at HAB drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the HAB drive is running forward. The limit switch will be muted for a short time only. |  |  |  | 380 | [DFR031]GAPCLO6_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
381 | Limit Switch | 45231010 | Infeed HAB shuttle at main drive limit switch | The HAB shuttle is at the limit switch which is activated if the main chain drive is running forward. |  |  |  | 381 | [DFR031]GAPCLO6_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
382 | Limit Switch | 45231011 | Infeed HAB shuttle at HAB drive limit switch | The HAB shuttle is at the limit switch which is activated if the HAB drive is running forward. |  |  |  | 382 | [DFR031]SFT_GAPCLO6_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
383 | Limit Switch | 45231995 | Not displayed on HMI! | (Prevent Jog Chain) |  |  |  | 383 | [DFR031]GAPCLO6_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
384 | Limit Switch | 45231996 | Not displayed on HMI! | (Prevent Jog HAB) |  |  |  | 384 | [DFR031]GAPCLO6_Ctr_ErrIface.b_JamAtDischargeBelt | 1 | 10.168.100.32 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
385 | DAI/Row Detection | 45235004 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed. |  |  |  | 385 | [DFR031]GAPCLO6_Ctr_ErrIface.b_NeedHomeOrSynch | 1 | 10.168.100.32 | A part is not homed | The home procedure has not been carried out yet.
386 | DAD/SM | 46010000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 386 | [DFR031]GAPCLO6_Ctr_ErrIface.b_IsHomingOrSynch | 1 | 10.168.100.32 | Homing active | The feeding system is homing or synchronising
387 | DAD/SM | 46010001 | Service mode active | The discharge of the buffer is in service mode. No production active. |  |  |  | 387 | [DFR031]H6_SMCtr_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
388 | DAD/SM | 46010002 | Calculation active | The unit is in calculation state. |  |  |  | 388 | [DFR031]H6_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
389 | DAD/SM | 46010003 | Unit switched off | The unit is disabled. |  |  |  | 389 | [DFR031]GAPCLO6_AxDischBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
390 | DAD/SM | 46010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing. |  |  |  | 390 | [DFR031]GAPCLO6_AxDischBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
391 | DAD/SM | 46010006 | Deactivated | The discharge is deactivated. No rows will be discharged. |  |  |  | 391 | [DFR031]GAPCLO6_AxDischBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
392 | DAD/Saf/Bottom | 46020010 | Door open left |  |  |  |  | 392 | [DFR031]GAPCLO6_AxDischBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
393 | DAD/Saf/Bottom | 46020011 | Door open right |  |  |  |  | 393 | [DFR031]GAPCLO6_AxDischBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
394 | DAD/Saf/Bottom | 46020017 | Muting fault | Cleaning mute failed. |  |  |  | 394 | [DFR031]GAPCLO6_AxBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
395 | DAD/Saf/Bottom | 46020018 | Doors open requested | The door will be unlocked if the last move is done. |  |  |  | 395 | [DFR031]GAPCLO6_AxBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
396 | DAD/Saf/Top | 46020020 | Door open left |  |  |  |  | 396 | [DFR031]GAPCLO6_AxBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
397 | DAD/Saf/Top | 46020021 | Door open right |  |  |  |  | 397 | [DFR031]GAPCLO6_AxBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
398 | DAD/Saf/Top | 46020028 | Doors open requested | The door will be unlocked if the last move is done. |  |  |  | 398 | [DFR031]GAPCLO6_AxBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
399 | DAD/Saf | 46020060 | Energize drives fault | The energizing of the drive is faulted. |  |  |  | 399 | [DFR031]GAPCLO6_AxBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
400 | DAD/Saf | 46020090 | Exhaust valve fault | The exhaust valve has a fault. |  |  |  | 400 | [DFR031]GAPCLO6_AxBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
401 | DAD/Saf | 46020091 | Restarting exhaust valve | The exhaust valve is restarting. |  |  |  | 401 | [DFR031]GAPCLO6_AxBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
402 | DAD/Saf | 46020092 | Energize exhaust valve fault | The energizing of the valve is faulted. |  |  |  | 402 | [DFR031]GAPCLO6_AxBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
403 | DAD/Saf | 46020093 | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 403 | [DFR031]GAPCLO6_AxBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
404 | DAD/Saf | 46020094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system. |  |  |  | 404 | [DFR031]GAPCLO7_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
405 | DAD/Downstream Interface | 46031005 | Setpoint simulation active | Setpoint simulation at discharge of buffer is switched on. |  |  |  | 405 | [DFR031]GAPCLO7_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
406 | DAD/Downstream Interface | 46031006 | Wrong fill level for setpoint | The proportion of parameters for calculating the setpoint to the downstream machine are not correct. |  |  |  | 406 | [DFR031]SFT_GAPCLO7_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
407 | DAD/Downstream Interface | 46031010 | Discharge 1 not ready | The corresponding distribution leg is not ready. |  |  |  | 407 | [DFR031]GAPCLO7_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
408 | DAD/Downstream Interface | 46031011 | Ethernet communication fault with leg 1 | An ethernet fault with the packaging leg is active. |  |  |  | 408 | [DFR031]GAPCLO7_Ctr_ErrIface.b_JamAtDischargeBelt | 1 | 10.168.100.32 | Jam at discharge belt | A jam on the discharge belt after the unit has occured.
409 | DAD/Downstream Interface | 46031012 | Discharge 1 disabled | The downstream interface is disabled. |  |  |  | 409 | [DFR031]GAPCLO7_Ctr_ErrIface.b_NeedHomeOrSynch | 1 | 10.168.100.32 | A part is not homed | The home procedure has not been carried out yet.
410 | DAD/Downstream Interface | 46031013 | Mc simulation discharge 1 active | Machine simulation at discharge of buffer is switched on. |  |  |  | 410 | [DFR031]GAPCLO7_Ctr_ErrIface.b_IsHomingOrSynch | 1 | 10.168.100.32 | Homing active | The feeding system is homing or synchronising
411 | DAD/Downstream Interface | 46031020 | Discharge 2 not ready | The corresponding distribution leg is not ready. |  |  |  | 411 | [DFR031]H7_SMCtr_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | Description: the unit and the corresponding controlled leg belts are in service mode. No rows will be distributed to this leg.
412 | DAD/Downstream Interface | 46031021 | Ethernet communication fault with leg 2 | An ethernet fault with the packaging leg is active. |  |  |  | 412 | [DFR031]H7_SMCtr_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode active | Description: the unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
413 | DAD/Downstream Interface | 46031022 | Discharge 2 disabled | The downstream interface is disabled. |  |  |  | 413 | [DFR031]GAPCLO7_AxDischBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
414 | DAD/Downstream Interface | 46031023 | Mc simulation discharge 2 active | Machine simulation at discharge of buffer is switched on. |  |  |  | 414 | [DFR031]GAPCLO7_AxDischBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
415 | DAD/Ctr | 46200000 | Sensor shelf in pos at pusher 1 not ready | The sensor shelf in position at the pusher of the discharge is not working properly or is either dirty or misadjusted or the gondola is either not mounted properly or has stopped at a wrong position. |  |  |  | 415 | [DFR031]GAPCLO7_AxDischBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
416 | DAD/Ctr | 46200001 | Sensor shelf in pos at pusher 2 not ready | The sensor shelf in position at the pusher of the discharge is not working properly or is either dirty or misadjusted or the gondola is either not mounted properly or has stopped at a wrong position. |  |  |  | 416 | [DFR031]GAPCLO7_AxDischBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
417 | DAD/Ctr | 46200003 | Wrong move distance calculated | The cotroller calculated a move distance which is too big. |  |  |  | 417 | [DFR031]GAPCLO7_AxDischBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
418 | DAD/Ctr | 46200005 | Minimum working level active | Discharge will start again if filling level is above a certain limit. |  |  |  | 418 | [DFR031]GAPCLO7_AxBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
419 | DAD/Ctr | 46200007 | Shuttle at top proximity switch | If the shuttle is at the top proximity switch, the discharge is blocked. It will not start moving again before the proximity switch is not activated any more and the minimum level for re-starting the discharge has been reached (hysteresis). |  |  |  | 419 | [DFR031]GAPCLO7_AxBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
420 | DAD/Ctr | 46200010 | Validation fault | The module detected a value out of range. |  |  |  | 420 | [DFR031]GAPCLO7_AxBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
421 | DAD/Ctr | 46200013 | Wrong stabilization time pusher 1 | The product parameter for row stabilization time on the discharge belt is not in a valid range. |  |  |  | 421 | [DFR031]GAPCLO7_AxBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
422 | DAD/Ctr | 46200014 | Wrong stabilization time pusher 2 | The product parameter for row stabilization time on the discharge belt is not in a valid range. |  |  |  | 422 | [DFR031]GAPCLO7_AxBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
423 | DAD/Ctr | 46200016 | Discharge belt 1 not in working position | Move the discharge belt toward the buffer and lock it. |  |  |  | 423 | [DFR031]GAPCLO7_AxBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
424 | DAD/Ctr | 46200017 | Discharge belt 2 not in working position | Move the discharge belt toward the buffer and lock it. |  |  |  | 424 | [DFR031]GAPCLO7_AxBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
425 | DAD/Ctr | 46200020 | HAB shuttle at HAB drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the HAB drive is running forward. |  |  |  | 425 | [DFR031]GAPCLO7_AxBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
426 | DAD/Ctr | 46200021 | HAB shuttle at main drive proximity switch | The HAB shuttle is at the proximity switch which is activated if the main chain drive is running forward. |  |  |  | 426 | [DFR031]GAPCLO7_AxBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
427 | DAD/Chain | 46201000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 427 | [DFR031]GAPCLO7_AxBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
428 | DAD/Chain | 46201001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 428 | [DFR031]FXX1_AxTranspBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
429 | DAD/Chain | 46201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 429 | [DFR031]FXX1_AxTranspBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
430 | DAD/Chain | 46201003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 430 | [DFR031]FXX1_AxTranspBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
431 | DAD/Chain | 46201004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 431 | [DFR031]FXX1_AxTranspBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
432 | DAD/Chain | 46201006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 432 | [DFR031]FXX1_AxTranspBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
433 | DAD/Chain | 46201010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 433 | [DFR031]FXX1_AxTranspBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
434 | DAD/Chain | 46201012 | Home sensor error | The home sensor has not detected any gondola during normal run. |  |  |  | 434 | [DFR031]FXX1_AxTranspBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
435 | DAD/HAB | 46202000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 435 | [DFR031]FXX1_AxTranspBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
436 | DAD/HAB | 46202001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 436 | [DFR031]FXX1_AxTranspBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
437 | DAD/HAB | 46202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 437 | [DFR031]FXX1_AxTranspBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
438 | DAD/HAB | 46202003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 438 | [DFR031]FXX1_AxTranspBlt3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
439 | DAD/HAB | 46202004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 439 | [DFR031]FXX1_AxTranspBlt3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
440 | DAD/HAB | 46202006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 440 | [DFR031]FXX1_AxTranspBlt3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
441 | DAD/HAB | 46202010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 441 | [DFR031]FXX1_AxTranspBlt3_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
442 | DAD/HAB | 46202013 | Wrong speed | This is a validation error. A speed or the proportional factor to calculate the speed are incorrect. |  |  |  | 442 | [DFR031]FXX1_AxTranspBlt3_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
443 | DAD/Pusher 1 | 46210000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 443 | [DFR031]FXX2_AxTranspBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
444 | DAD/Pusher 1 | 46210001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 444 | [DFR031]FXX2_AxTranspBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
445 | DAD/Pusher 1 | 46210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 445 | [DFR031]FXX2_AxTranspBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
446 | DAD/Pusher 1 | 46210003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 446 | [DFR031]FXX2_AxTranspBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
447 | DAD/Pusher 1 | 46210004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 447 | [DFR031]FXX2_AxTranspBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
448 | DAD/Pusher 1 | 46210006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 448 | [DFR031]FXX2_AxTranspBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
449 | DAD/Pusher 1 | 46210010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 449 | [DFR031]FXX2_AxTranspBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
450 | DAD/Pusher 1 | 46210011 | Not in working area | The pusher ist not in the working area. Chain and pusher moves are not possible. |  |  |  | 450 | [DFR031]FXX2_AxTranspBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
451 | DAD/Pusher 1 | 46210012 | Home sensor error | The home sensor is not working properly. |  |  |  | 451 | [DFR031]FXX2_AxTranspBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
452 | DAD/Pusher 1 | 46210013 | Wrong position | This is a validation error. Front or rear position are incorrect. |  |  |  | 452 | [DFR031]FXX2_AxTranspBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
453 | DAD/Pusher 2 | 46211000 | Drive fault | The drive controller of this motor is reporting a fault condition. |  |  |  | 453 | [DFR031]FXX2_AxTranspBlt3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
454 | DAD/Pusher 2 | 46211001 | Position error | The controlled motor is out of the commanded position. |  |  |  | 454 | [DFR031]FXX2_AxTranspBlt3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
455 | DAD/Pusher 2 | 46211002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded. |  |  |  | 455 | [DFR031]FXX2_AxTranspBlt3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
456 | DAD/Pusher 2 | 46211003 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect. |  |  |  | 456 | [DFR031]FXX2_AxTranspBlt3_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
457 | DAD/Pusher 2 | 46211004 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off. |  |  |  | 457 | [DFR031]FXX2_AxTranspBlt3_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
458 | DAD/Pusher 2 | 46211006 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit. |  |  |  | 458 | [DFR031]FXX3_AxTranspBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
459 | DAD/Pusher 2 | 46211010 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed. |  |  |  | 459 | [DFR031]FXX3_AxTranspBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
460 | DAD/Pusher 2 | 46211011 | Not in working area | The pusher ist not in the working area. Chain and pusher moves are not possible. |  |  |  | 460 | [DFR031]FXX3_AxTranspBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
461 | DAD/Pusher 2 | 46211012 | Home sensor error | The home sensor is not working properly. |  |  |  | 461 | [DFR031]FXX3_AxTranspBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
462 | DAD/Pusher 2 | 46211013 | Wrong position | This is a validation error. Front or rear position are incorrect. |  |  |  | 462 | [DFR031]FXX3_AxTranspBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
463 | DAD/Backstop 1 | 46216004 | Switched off | The device has been switched off. |  |  |  | 463 | [DFR031]FXX3_AxTranspBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
464 | DAD/Backstop 1 | 46216012 | Proximity switch not found | The proximity limit switch of the device is not working correctly. |  |  |  | 464 | [DFR031]FXX3_AxTranspBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
465 | DAD/Backstop 2 | 46217004 | Switched off | The device has been switched off. |  |  |  | 465 | [DFR031]FXX3_AxTranspBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
466 | DAD/Backstop 2 | 46217012 | Proximity switch not found | The proximity limit switch of the device is not working correctly. |  |  |  | 466 | [DFR031]FXX3_AxTranspBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
467 | Limit Switch | 46231000 | Discharge HAB shuttle at main drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the main chain drive is running forward. The limit switch will be muted for a short time only. |  |  |  | 467 | [DFR031]FXX3_AxTranspBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
468 | Limit Switch | 46231001 | Discharge HAB shuttle at HAB drive limit switch muted | The HAB shuttle is at the limit switch which is activated if the HAB drive is running forward. The limit switch will be muted for a short time only. |  |  |  | 468 | [DFR031]FXX3_AxTranspBlt3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
469 | Limit Switch | 46231010 | Discharge HAB shuttle at main drive limit switch | The HAB shuttle at discharge is at the limit switch which is activated if the main chain drive is running forward. |  |  |  | 469 | [DFR031]FXX3_AxTranspBlt3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
470 | Limit Switch | 46231011 | Discharge HAB shuttle at HAB drive limit switch | The HAB shuttle at discharge is at the limit switch which is activated if the HAB drive is running forward. |  |  |  | 470 | [DFR031]FXX3_AxTranspBlt3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
471 | Limit Switch | 46231995 | Not displayed on HMI! | (Prevent Jog Chain) |  |  |  | 471 | [DFR031]FXX3_AxTranspBlt3_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
472 | Limit Switch | 46231996 | Not displayed on HMI! | (Prevent Jog HAB) |  |  |  | 472 | [DFR031]FXX3_AxTranspBlt3_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
473 | GMS |  | Air pressure too low | The air pressure is below the allowed operating level. |  |  |  | 473 | [DFR031]FXX4_AxTranspBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
[8 empty] | 474 | [DFR031]FXX4_AxTranspBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 481 | [DFR031]FXX4_AxTranspBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
Data# | Processor Tag |  | Value | Concentrator Tag | Path IP | Description | Python Variable Name | 482 | [DFR031]FXX4_AxTranspBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
1 | [DFR031]UIFACE_b_oHOLReady |  | 1 | ComData_DFR_To_Skynet.Status_Bits[0].0 | 10.168.100.34 | Belt Head of Line Ready |  | 483 | [DFR031]FXX4_AxTranspBlt3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
2 | [DFR031]UIFACE_b_oLineReady |  | 1 | ComData_DFR_To_Skynet.Status_Bits[0].1 | 10.168.100.34 | Line Ready |  | 484 | [DFR031]FXX4_AxTranspBlt3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
3 | [DFR031]BLTHOL_AxDdu1_Iface.b_RunInProd |  | 1 | ComData_DFR_To_Skynet.Status_Bits[0].2 | 10.168.100.34 | DDU1 In Production Mode |  | 485 | [DFR031]FXX4_AxTranspBlt3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
4 | [DFR031]CtrlIface.b_AlarmActive |  | 1 | ComData_DFR_To_Skynet.Status_Bits[0].10 | 10.168.100.34 | Alarm Present |  | 493 | [DFR031]FXX5_AxTranspBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
5 | [DFR031]HMI_Cmd.BtnEnShift1.b_Active |  | 1 | ComData_DFR_To_Skynet.Status_Bits[0].11 | 10.168.100.34 | Shift 1 Enabled |  | 494 | [DFR031]FXX5_AxTranspBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
6 | [DFR031]HMI_Cmd.BtnEnShift2.b_Active |  | 1 | ComData_DFR_To_Skynet.Status_Bits[0].12 | 10.168.100.34 | Shift 2 Enabled |  | 495 | [DFR031]FXX5_AxTranspBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
7 | [DFR031]HMI_Cmd.BtnEnShift3.b_Active |  | 1 | ComData_DFR_To_Skynet.Status_Bits[0].13 | 10.168.100.34 | Shift 3 Enabled |  | 496 | [DFR031]FXX5_AxTranspBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
8 | [7 empty] | 497 | [DFR031]FXX5_AxTranspBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
9 | [DFR031]INFO_Hmi.ProdCounter.dn_RowInfeed |  | Var | ComData_DFR_To_Skynet.Status_Bits[10] | 10.168.100.34 | Rows into DFR | dfr_031_rows_into_dfr | 498 | [DFR031]FXX5_AxTranspBlt3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
10 | [DFR031]INFO_Hmi.StatisticsCounter.dn_RowManualDump |  | Var | ComData_DFR_To_Skynet.Status_Bits[11] | 10.168.100.34 | Rows Manually Dumped | dfr_031_rows_manually_dumped | 499 | [DFR031]FXX5_AxTranspBlt3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
11 | [DFR031]INFO_Hmi.StatisticsCounter.dn_RowTooSmall |  | Var | ComData_DFR_To_Skynet.Status_Bits[12] | 10.168.100.34 | Rows Dumped Row Too Small | dfr_031_rows_dumped_row_too_small | 500 | [DFR031]FXX5_AxTranspBlt3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
12 | [DFR031]INFO_Hmi.StatisticsCounter.dn_RowTooLong |  | Var | ComData_DFR_To_Skynet.Status_Bits[13] | 10.168.100.34 | Rows Dumped Row Too Long | dfr_031_rows_dumped_row_too_long | 501 | [DFR031]FXX5_AxTranspBlt3_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
13 | [DFR031]INFO_Hmi.StatisticsCounter.dn_RowTooHigh |  | Var | ComData_DFR_To_Skynet.Status_Bits[14] | 10.168.100.34 | Rows Dumped Row Too High | dfr_031_rows_dumped_row_too_high | 502 | [DFR031]FXX5_AxTranspBlt3_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
14 | [DFR031]INFO_Hmi.StatisticsCounter.dn_GapTooSmall |  | Var | ComData_DFR_To_Skynet.Status_Bits[15] | 10.168.100.34 | Rows Dumped Gap Too Small | dfr_031_rows_dumped_gap_too_small | 503 | [DFR031]FXX6_AxTranspBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
15 | [DFR031]INFO_Hmi.StatisticsCounter.dn_RowPosNotValid |  | Var | ComData_DFR_To_Skynet.Status_Bits[16] | 10.168.100.34 | Rows Dumped Row Out of Position | dfr_031_rows_dumped_row_out_of_position | 504 | [DFR031]FXX6_AxTranspBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
16 | [DFR031]INFO_Hmi.StatisticsCounter.dn_DwnstrNotReady |  | Var | ComData_DFR_To_Skynet.Status_Bits[17] | 10.168.100.34 | Rows Dumped Downstream Not Ready | dfr_031_rows_dumped_downstream_not_ready | 505 | [DFR031]FXX6_AxTranspBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
17 | [DFR031]INFO_Hmi.StatisticsCounter.dn_NotRun |  | Var | ComData_DFR_To_Skynet.Status_Bits[18] | 10.168.100.34 | Rows Dumped Not in Run | dfr_031_rows_dumped_not_in_run | 506 | [DFR031]FXX6_AxTranspBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
18 | [DFR031]INFO_Hmi.ProdCounter.dn_RowDistribDA1 |  | Var | ComData_DFR_To_Skynet.Status_Bits[19] | 10.168.100.34 | Rows Distributed into Buffer | dfr_031_rows_distributed_into_buffer | 507 | [DFR031]FXX6_AxTranspBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
19 | [DFR031]INFO_Hmi.ProdCounter.dn_RowDistribPusher1 |  | Var | ComData_DFR_To_Skynet.Status_Bits[20] | 10.168.100.34 | Rows Distributed to Sig 1 | dfr_031_rows_distributed_to_sig_1 | 508 | [DFR031]FXX6_AxTranspBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
20 | [DFR031]INFO_Hmi.ProdCounter.dn_RowDistribPusher2 |  | Var | ComData_DFR_To_Skynet.Status_Bits[21] | 10.168.100.34 | Rows Distributed to Sig 2 | dfr_031_rows_distributed_to_sig_2
| [DFR031]DA_Ctr_Iface.dn_FillingLevelPercent |  | Var | ComData_DFR_To_Skynet.Status_Bits[22] | 10.168.100.34 | Buffer Fill Level | dfr_031_buffer_fill_level
21 | [DFR031]HMI_Cmd.Dn_StartHoursShift1 |  | Var | ComData_DFR_To_Skynet.Parameters[0] | 10.168.100.34 | Start Time Hours Shift 1 |  | 509 | [DFR031]FXX6_AxTranspBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
22 | [DFR031]HMI_Cmd.Dn_StartMinutesShift1 |  | Var | ComData_DFR_To_Skynet.Parameters[1] | 10.168.100.34 | Start Time Minutes Shift 1 |  | 510 | [DFR031]FXX6_AxTranspBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
23 | [DFR031]HMI_Cmd.Dn_StartHoursShift2 |  | Var | ComData_DFR_To_Skynet.Parameters[2] | 10.168.100.34 | Start Time Hours Shift 2 |  | 511 | [DFR031]FXX6_AxTranspBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
24 | [DFR031]HMI_Cmd.Dn_StartMinutesShift2 |  | Var | ComData_DFR_To_Skynet.Parameters[3] | 10.168.100.34 | Start Time Minutes Shift 2 |  | 512 | [DFR031]FXX6_AxTranspBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
25 | [DFR031]HMI_Cmd.Dn_StartHoursShift3 |  | Var | ComData_DFR_To_Skynet.Parameters[4] | 10.168.100.34 | Start Time Hours Shift 3 |  | 513 | [DFR031]FXX6_AxTranspBlt3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
26 | [DFR031]HMI_Cmd.Dn_StartMinutesShift3 |  | Var | ComData_DFR_To_Skynet.Parameters[5] | 10.168.100.34 | Start Time Minutes Shift 3 |  | 514 | [DFR031]FXX6_AxTranspBlt3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
27 | [DFR031]HMI_Cmd.Dn_EndHoursShift1 |  | Var | ComData_DFR_To_Skynet.Parameters[6] | 10.168.100.34 | End Time Hours Shift 1 |  | 515 | [DFR031]FXX6_AxTranspBlt3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
28 | [DFR031]HMI_Cmd.Dn_EndMinutesShift1 |  | Var | ComData_DFR_To_Skynet.Parameters[7] | 10.168.100.34 | End Time Minutes Shift 1 |  | 516 | [DFR031]FXX6_AxTranspBlt3_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
29 | [DFR031]HMI_Cmd.Dn_EndHoursShift2 |  | Var | ComData_DFR_To_Skynet.Parameters[8] | 10.168.100.34 | End Time Hours Shift 2 |  | 517 | [DFR031]FXX6_AxTranspBlt3_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
30 | [DFR031]HMI_Cmd.Dn_EndMinutesShift2 |  | Var | ComData_DFR_To_Skynet.Parameters[9] | 10.168.100.34 | End Time Minutes Shift 2 |  | 518 | [DFR031]FXX7_AxTranspBlt1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
31 | [DFR031]HMI_Cmd.Dn_EndHoursShift3 |  | Var | ComData_DFR_To_Skynet.Parameters[10] | 10.168.100.34 | End Time Hours Shift 3 |  | 519 | [DFR031]FXX7_AxTranspBlt1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
32 | [DFR031]HMI_Cmd.Dn_EndMinutesShift3 |  | Var | ComData_DFR_To_Skynet.Parameters[11] | 10.168.100.34 | End Time Minutes Shift 3 |  | 520 | [DFR031]FXX7_AxTranspBlt1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
33 | [DFR031]HMI_dn_Hour |  | Var | ComData_DFR_To_Skynet.Parameters[12] | 10.168.100.34 | Current Hour In Processor |  | 521 | [DFR031]FXX7_AxTranspBlt1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
34 | [DFR031]HMI_dn_Minute |  | Var | ComData_DFR_To_Skynet.Parameters[13] | 10.168.100.34 | Current Minute In Processor |  | 522 | [DFR031]FXX7_AxTranspBlt1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
35 | [DFR031]SM.Errors.DynText.List[0].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[0] | 10.168.100.34 | Dynamic Text Fault List 0 |  | 523 | [DFR031]FXX7_AxTranspBlt2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
36 | [DFR031]SM.Errors.DynText.List[1].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[1] | 10.168.100.34 | Dynamic Text Fault List 1 |  | 524 | [DFR031]FXX7_AxTranspBlt2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
37 | [DFR031]SM.Errors.DynText.List[2].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[2] | 10.168.100.34 | Dynamic Text Fault List 2 |  | 525 | [DFR031]FXX7_AxTranspBlt2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
38 | [DFR031]SM.Errors.DynText.List[3].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[3] | 10.168.100.34 | Dynamic Text Fault List 3 |  | 526 | [DFR031]FXX7_AxTranspBlt2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
39 | [DFR031]SM.Errors.DynText.List[4].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[4] | 10.168.100.34 | Dynamic Text Fault List 4 |  | 527 | [DFR031]FXX7_AxTranspBlt2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
40 | [DFR031]SM.Errors.DynText.List[5].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[5] | 10.168.100.34 | Dynamic Text Fault List 5 |  | 528 | [DFR031]FXX7_AxTranspBlt3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
41 | [DFR031]SM.Errors.DynText.List[6].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[6] | 10.168.100.34 | Dynamic Text Fault List 6 |  | 529 | [DFR031]FXX7_AxTranspBlt3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
42 | [DFR031]SM.Errors.DynText.List[7].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[7] | 10.168.100.34 | Dynamic Text Fault List 7 |  | 530 | [DFR031]FXX7_AxTranspBlt3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
43 | [DFR031]SM.Errors.DynText.List[8].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[8] | 10.168.100.34 | Dynamic Text Fault List 8 |  | 531 | [DFR031]FXX7_AxTranspBlt3_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a value out of range.
44 | [DFR031]SM.Errors.DynText.List[9].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[9] | 10.168.100.34 | Dynamic Text Fault List 9 |  | 532 | [DFR031]FXX7_AxTranspBlt3_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | The motor has been switched off temporarily.
45 | [DFR031]SM.Errors.FixText.List[0].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[30] | 10.168.100.34 | Fixed Text Fault List 0 |  | 553 | [DFR031]ALN1_Ax_ErrIface.b_AlignTooSlow | 1 | 10.168.100.32 | Cycle time of the aligner too long | This is a validation error. The aligner needs too long for a cycle. Increase speeds and acc/dec to speed-up the aligner.
46 | [DFR031]SM.Errors.FixText.List[1].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[31] | 10.168.100.34 | Fixed Text Fault List 1 |  | 554 | [DFR031]ALN1_Ax_ErrIface.b_AlignEyeTooClose | 1 | 10.168.100.32 | Wrong aligner distance | This is a validation error. The aligner is too close to its start position.
47 | [DFR031]SM.Errors.FixText.List[2].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[32] | 10.168.100.34 | Fixed Text Fault List 2 |  | 555 | [DFR031]ALN1_Ax_ErrIface.b_EndMovToFast | 1 | 10.168.100.32 | End move is too fast | This is a validation error. If the option clever aligning is on we have to move into the gap directly - without waiting in the open position. If the last move is too fast we would touch the rear edge of the row.
48 | [DFR031]SM.Errors.FixText.List[3].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[33] | 10.168.100.34 | Fixed Text Fault List 3 |  | 556 | [DFR031]ALN1_Ax_ErrIface.b_AdjustmentFault | 1 | 10.168.100.32 | Adjustment error | This is an adjustment error. One of the values is out of range.
49 | [DFR031]SM.Errors.FixText.List[4].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[34] | 10.168.100.34 | Fixed Text Fault List 4 |  | 557 | [DFR031]ALN1_Ax_ErrIface.b_CheckPhotoeyeWarn | 1 | 10.168.100.32 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
50 | [DFR031]SM.Errors.FixText.List[5].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[35] | 10.168.100.34 | Fixed Text Fault List 5 |  | 558 | [DFR031]ALN1_Ax_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
51 | [DFR031]SM.Errors.FixText.List[6].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[36] | 10.168.100.34 | Fixed Text Fault List 6 |  | 559 | [DFR031]ALN1_Ax_ErrIface.b_RowSim | 1 | 10.168.100.32 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
52 | [DFR031]SM.Errors.FixText.List[7].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[37] | 10.168.100.34 | Fixed Text Fault List 7 |  | 560 | [DFR031]ALN1_Ax_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
53 | [DFR031]SM.Errors.FixText.List[8].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[38] | 10.168.100.34 | Fixed Text Fault List 8 |  | 561 | [DFR031]ALN1_Ax_ErrIface.b_HomeNeeded | 1 | 10.168.100.32 | Home needed | The aligner is stopping to home after restart.
54 | [DFR031]SM.Errors.FixText.List[9].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[39] | 10.168.100.34 | Fixed Text Fault List 9 |  | 562 | [DFR031]ALN1_Ax_ErrIface.b_MaxPosStopTime | 1 | 10.168.100.32 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
55 | [DFR031]SM.Errors.FixText.List[10].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[40] | 10.168.100.34 | Fixed Text Fault List 10 |  | 563 | [DFR031]ALN1_Ax_ErrIface.b_ProdTooHigh | 1 | 10.168.100.32 | Product too high | There is a too high product detected in front of the aligner.
56 | [DFR031]SM.Errors.FixText.List[11].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[41] | 10.168.100.34 | Fixed Text Fault List 11 |  | 564 | [DFR031]ALN1_Pneum_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
57 | [DFR031]SM.Errors.FixText.List[12].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[42] | 10.168.100.34 | Fixed Text Fault List 12 |  | 565 | [DFR031]ALN1_Pneum_ErrIface.b_CheckPhotoeyeWarn | 1 | 10.168.100.32 | Warning photoeye is not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
58 | [DFR031]SM.Errors.FixText.List[13].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[43] | 10.168.100.34 | Fixed Text Fault List 13 |  | 566 | [DFR031]ALN1_Pneum_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
59 | [DFR031]SM.Errors.FixText.List[14].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[44] | 10.168.100.34 | Fixed Text Fault List 14 |  | 567 | [DFR031]ALN1_Pneum_ErrIface.b_RowSim | 1 | 10.168.100.32 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
60 | [DFR031]SM.Errors.FixText.List[15].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[45] | 10.168.100.34 | Fixed Text Fault List 15 |  | 568 | [DFR031]ALN2_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
61 | [DFR031]SM.Errors.FixText.List[16].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[46] | 10.168.100.34 | Fixed Text Fault List 16 |  | 569 | [DFR031]ALN2_SM_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | The aligner is in service mode. No aligning possible.
62 | [DFR031]SM.Errors.FixText.List[17].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[47] | 10.168.100.34 | Fixed Text Fault List 17 |  | 570 | [DFR031]ALN2_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
63 | [DFR031]SM.Errors.FixText.List[18].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[48] | 10.168.100.34 | Fixed Text Fault List 18 |  | 571 | [DFR031]ALN2_SM_ErrIface.b_StateMachineDisabled | 1 | 10.168.100.32 | Switched off | The aligner is disabled.
64 | [DFR031]SM.Errors.FixText.List[19].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[49] | 10.168.100.34 | Fixed Text Fault List 19 |  | 572 | [DFR031]ALN2_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
65 | [DFR031]SM.Errors.FixText.List[20].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[50] | 10.168.100.34 | Fixed Text Fault List 20 |  | 573 | [DFR031]SFT_ALN2_Saf_ErrIface.Cover.b_DeEnergized | 1 | 10.168.100.32 | cover open | There is a guard on the machine which is open.
66 | [DFR031]SM.Errors.FixText.List[21].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[51] | 10.168.100.34 | Fixed Text Fault List 21 |  | 574 | [DFR031]ALN2_Saf_ErrIface.b_CoverOpenRequested | 1 | 10.168.100.32 | cover open requested | The guard will be open if the last move is done.
67 | [DFR031]SM.Errors.FixText.List[22].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[52] | 10.168.100.34 | Fixed Text Fault List 22 |  | 575 | [DFR031]SFT_ALN2_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drive fault | The energizing of the drive is faulted.
68 | [DFR031]SM.Errors.FixText.List[23].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[53] | 10.168.100.34 | Fixed Text Fault List 23 |  | 576 | [DFR031]ALN2_Saf_ErrIface.b_ExhaustValveFault | 1 | 10.168.100.32 | Exhaust valve fault | The exhaust valve has a fault.
69 | [DFR031]SM.Errors.FixText.List[24].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[54] | 10.168.100.34 | Fixed Text Fault List 24 |  | 577 | [DFR031]ALN2_Saf_ErrIface.b_RestartingExhaustValve | 1 | 10.168.100.32 | Restarting exhaust valve | The exhaust valve is restarting.
70 | [DFR031]SM.Errors.FixText.List[25].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[55] | 10.168.100.34 | Fixed Text Fault List 25 |  | 578 | [DFR031]SFT_ALN2_Saf_ErrIface.EnergizeExhaustValve.b_DeEnergized | 1 | 10.168.100.32 | Energize exhaust valve fault | The energizing of the valve is faulted.
71 | [DFR031]SM.Errors.FixText.List[26].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[56] | 10.168.100.34 | Fixed Text Fault List 26 |  | 579 | [DFR031]ALN2_Saf_ErrIface.b_NoCompAir | 1 | 10.168.100.32 | Air pressure too low | The air pressure is below the allowed operating level.
72 | [DFR031]SM.Errors.FixText.List[27].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[57] | 10.168.100.34 | Fixed Text Fault List 27 |  | 580 | [DFR031]ALN2_Saf_ErrIface.b_CompAirNotExhausted | 1 | 10.168.100.32 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
73 | [DFR031]SM.Errors.FixText.List[28].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[58] | 10.168.100.34 | Fixed Text Fault List 28 |  | 581 | [DFR031]ALN2_Ax_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
74 | [DFR031]SM.Errors.FixText.List[29].dn_ID |  | Var | ComData_DFR_To_Skynet.Fault_data[59] | 10.168.100.34 | Fixed Text Fault List 29 |  | 582 | [DFR031]ALN2_Ax_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
75 |  |  | Var |  | 10.168.100.35 |  |  | 583 | [DFR031]ALN2_Ax_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
76 | [DFR031]SM.Errors.DynText.dn_LastPos |  | Var | ComData_DFR_To_Skynet.Fault_data[60] | 10.168.100.34 | Position of Last stored position in Dyn List |  | 584 | [DFR031]ALN2_Ax_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation error | This is a validation error. One of the values is out of range.
77 | [DFR031]SM.Errors.FixText.dn_LastPos |  | Var | ComData_DFR_To_Skynet.Fault_data[61] | 10.168.100.34 | Position of Last stored position in Fix List |  | 585 | [DFR031]ALN2_Ax_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
78 | [DFR031]SM.Errors.DynText.dn_EmptyPos |  | Var | ComData_DFR_To_Skynet.Fault_data[62] | 10.168.100.34 | Position of Next stored position in Dyn List |  | 586 | [DFR031]ALN2_Ax_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the aligner cannot be synchronized in the set time limit.
79 | [DFR031]SM.Errors.FixText.dn_EmptyPos |  | Var | ComData_DFR_To_Skynet.Fault_data[63] | 10.168.100.34 | Position of Next stored position in Fix List |  | 587 | [DFR031]ALN2_Ax_ErrIface.b_AccDecError | 1 | 10.168.100.32 | Acc / Dec out of range | This is a validation error. Acceleration / deceleration out of range (bigger than maximum, or less than the minimum required to decelerate after aligning into the open position).
[8 empty] | 588 | [DFR031]ALN2_Ax_ErrIface.b_AlignTooSlow | 1 | 10.168.100.32 | Cycle time of the aligner too long | This is a validation error. The aligner needs too long for a cycle. Increase speeds and acc/dec to speed-up the aligner.
[8 empty] | 589 | [DFR031]ALN2_Ax_ErrIface.b_AlignEyeTooClose | 1 | 10.168.100.32 | Wrong aligner distance | This is a validation error. The aligner is too close to its start position.
[8 empty] | 590 | [DFR031]ALN2_Ax_ErrIface.b_EndMovToFast | 1 | 10.168.100.32 | End move is too fast | This is a validation error. If the option clever aligning is on we have to move into the gap directly - without waiting in the open position. If the last move is too fast we would touch the rear edge of the row.
[8 empty] | 591 | [DFR031]ALN2_Ax_ErrIface.b_AdjustmentFault | 1 | 10.168.100.32 | Adjustment error | This is an adjustment error. One of the values is out of range.
[8 empty] | 592 | [DFR031]ALN2_Ax_ErrIface.b_CheckPhotoeyeWarn | 1 | 10.168.100.32 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
[8 empty] | 593 | [DFR031]ALN2_Ax_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
[8 empty] | 594 | [DFR031]ALN2_Ax_ErrIface.b_RowSim | 1 | 10.168.100.32 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
[8 empty] | 595 | [DFR031]ALN2_Ax_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
[8 empty] | 596 | [DFR031]ALN2_Ax_ErrIface.b_HomeNeeded | 1 | 10.168.100.32 | Home needed | The aligner is stopping to home after restart.
[8 empty] | 597 | [DFR031]ALN2_Ax_ErrIface.b_MaxPosStopTime | 1 | 10.168.100.32 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
[8 empty] | 598 | [DFR031]ALN2_Ax_ErrIface.b_ProdTooHigh | 1 | 10.168.100.32 | Product too high | There is a too high product detected in front of the aligner.
[8 empty] | 599 | [DFR031]ALN2_Pneum_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 600 | [DFR031]ALN2_Pneum_ErrIface.b_CheckPhotoeyeWarn | 1 | 10.168.100.32 | Warning photoeye is not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
[8 empty] | 601 | [DFR031]ALN2_Pneum_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
[8 empty] | 602 | [DFR031]ALN2_Pneum_ErrIface.b_RowSim | 1 | 10.168.100.32 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
[8 empty] | 603 | [DFR031]DBP_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
[8 empty] | 604 | [DFR031]DBP_SM_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | The unit is in service mode. No production active.
[8 empty] | 605 | [DFR031]DBP_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
[8 empty] | 606 | [DFR031]DBP_SM_ErrIface.b_StateMachineDisabled | 1 | 10.168.100.32 | Unit switched off | The unit is disabled.
[8 empty] | 607 | [DFR031]DBP_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
[8 empty] | 608 | [DFR031]DBP_AxPuln_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
[8 empty] | 609 | [DFR031]DBP_AxPuln_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 610 | [DFR031]DBP_AxPuln_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 611 | [DFR031]DBP_AxPuln_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 612 | [DFR031]DBP_AxPuln_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 613 | [DFR031]DBP_AxPuln_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
[8 empty] | 614 | [DFR031]DBP_AxPuln_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
[8 empty] | 615 | [DFR031]DBP_AxPuln_ErrIface.b_NegOvertravel | 1 | 10.168.100.32 | Negative overtravel | The axis has exceeded the software limit position in negative direction.
[8 empty] | 616 | [DFR031]DBP_AxPuln_ErrIface.b_PosOvertravel | 1 | 10.168.100.32 | Positive overtravel | The axis has exceeded the software limit position in positive direction.
[8 empty] | 617 | [DFR031]DBP_AxPuln_ErrIface.b_AdjustmentFault | 1 | 10.168.100.32 | Adjustment error | This is an adjustment error. One of the values is out of range.
[8 empty] | 618 | [DFR031]DBP_AxPuln_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye not ok | Something with this photoeye is not ok (flickering, sees no product, ...).
[8 empty] | 619 | [DFR031]DBP_AxPuln_ErrIface.b_RowSim | 1 | 10.168.100.32 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
[8 empty] | 620 | [DFR031]BLTHOL_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
[8 empty] | 621 | [DFR031]BLTHOL_SM_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | The process belts are in service mode. No production possible
[8 empty] | 622 | [DFR031]BLTHOL_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
[8 empty] | 623 | [DFR031]BLTHOL_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
[8 empty] | 624 | [DFR031]BLTHOL_SM_ErrIface.b_CleanModeActive | 1 | 10.168.100.32 | Clean mode belts active | The process belts are in clean mode. No production possible.
[8 empty] | 625 | [DFR031]BLTHOL_SM_ErrIface.b_EmptyModeActive | 1 | 10.168.100.32 | Empty mode belts is active | The belt empty mode is active.
[8 empty] | 626 | [DFR031]SFT_BLTHOL_Saf_ErrIface.EnergizeDrivesRack1.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault Rack 1 | The energizing of the drive is faulted.
[8 empty] | 627 | [DFR031]SFT_BLTHOL_Saf_ErrIface.EnergizeDrivesRack2.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault Rack 2 | The energizing of the drive is faulted.
[8 empty] | 628 | [DFR031]SFT_BLTHOL_Saf_ErrIface.EnergizeBltTrackDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault belt track | The energizing of the belt track drive is faulted.
[8 empty] | 629 | [DFR031]BLTHOL_Saf_ErrIface.b_ExhaustValveFault | 1 | 10.168.100.32 | Exhaust valve fault | The exhaust valve has a fault.
[8 empty] | 630 | [DFR031]BLTHOL_Saf_ErrIface.b_RestartingExhaustValve | 1 | 10.168.100.32 | Restarting exhaust valve | The exhaust valve is restarting.
[8 empty] | 631 | [DFR031]SFT_BLTHOL_Saf_ErrIface.EnergizeExhaustValve.b_DeEnergized | 1 | 10.168.100.32 | Energize exhaust valve fault | The energizing of the valve is faulted.
[8 empty] | 632 | [DFR031]BLTHOL_Saf_ErrIface.b_NoCompAir | 1 | 10.168.100.32 | Air pressure too low | The air pressure is below the allowed operating level.
[8 empty] | 633 | [DFR031]BLTHOL_Saf_ErrIface.b_CompAirNotExhausted | 1 | 10.168.100.32 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
[8 empty] | 634 | [DFR031]SFT_BLTHOL_SafRCUL_ErrIface.EnergizeDrive.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
[8 empty] | 635 | [DFR031]SFT_BLTHOL_SafRCUL_ErrIface.WorkPos.b_DeEnergized | 1 | 10.168.100.32 | Not In working position | The belt is not in down position, therefore it is not possible to run the belt.
[8 empty] | 636 | [DFR031]SFT_BLTHOL_SafRCUR_ErrIface.EnergizeDrive.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
[8 empty] | 637 | [DFR031]SFT_BLTHOL_SafRCUR_ErrIface.WorkPos.b_DeEnergized | 1 | 10.168.100.32 | Not In working position | The belt is not in down position, therefore it is not possible to run the belt.
[8 empty] | 638 | [DFR031]BLTHOL_Ctr_ErrIface.b_DwnstrNotRdy | 1 | 10.168.100.32 | Downstream equipment not ready | The downstream equipment is not ready.
[8 empty] | 639 | [DFR031]BLTHOL_Ctr_ErrIface.b_EmptyBelts | 1 | 10.168.100.32 | Empty belts active until DDU1 | Upstream is not ready. No product is coming in from upstream.
[8 empty] | 640 | [DFR031]BLTHOL_Ctr_ErrIface.b_UpstrNotRdy | 1 | 10.168.100.32 | Not displayed on HMI!
[8 empty] | 641 | [DFR031]RR1_AxBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 642 | [DFR031]RR1_AxBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 643 | [DFR031]RR1_AxBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 644 | [DFR031]RR1_AxBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 645 | [DFR031]RR1_AxBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 646 | [DFR031]RR1_AxBlt_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye row detection is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
[8 empty] | 647 | [DFR031]RR1_AxBlt_ErrIface.b_AdjustmentFault | 1 | 10.168.100.32 | Adjustment fault | There is a functional fault. It is not possible to do the commanded function of the row regulation belt due to bad parameter settings.
[8 empty] | 648 | [DFR031]RR1_BltTrack_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 649 | [DFR031]RR1_BltTrack_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 650 | [DFR031]RR1_BltTrack_ErrIface.b_BltEdgeSensorFault | 1 | 10.168.100.32 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
[8 empty] | 651 | [DFR031]RR1_BltTrack_ErrIface.b_TrackMotorFault | 1 | 10.168.100.32 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked.
[8 empty] | 652 | [DFR031]RR2_AxBlt_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 653 | [DFR031]RR2_AxBlt_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 654 | [DFR031]RR2_AxBlt_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 655 | [DFR031]RR2_AxBlt_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 656 | [DFR031]RR2_AxBlt_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 657 | [DFR031]RR2_AxBlt_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye row detection is not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
[8 empty] | 658 | [DFR031]RR2_AxBlt_ErrIface.b_AdjustmentFault | 1 | 10.168.100.32 | Adjustment fault | There is a functional fault. It is not possible to do the commanded function of the row regulation belt due to bad parameter settings.
[8 empty] | 659 | [DFR031]RR2_BltTrack_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 660 | [DFR031]RR2_BltTrack_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 661 | [DFR031]RR2_BltTrack_ErrIface.b_BltEdgeSensorFault | 1 | 10.168.100.32 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
[8 empty] | 662 | [DFR031]RR2_BltTrack_ErrIface.b_TrackMotorFault | 1 | 10.168.100.32 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked.
[8 empty] | 663 | [DFR031]BLTHOL_AxU1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 664 | [DFR031]BLTHOL_AxU1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 665 | [DFR031]BLTHOL_AxU1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 666 | [DFR031]BLTHOL_AxU1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 667 | [DFR031]BLTHOL_AxU1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 668 | [DFR031]BLTHOL_AxU1_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 669 | [DFR031]BLTHOL_U1Track_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 670 | [DFR031]BLTHOL_U1Track_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 671 | [DFR031]BLTHOL_U1Track_ErrIface.b_BltEdgeSensorFault | 1 | 10.168.100.32 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
[8 empty] | 672 | [DFR031]BLTHOL_U1Track_ErrIface.b_TrackMotorFault | 1 | 10.168.100.32 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked.
[8 empty] | 673 | [DFR031]BLTHOL_AxU1Left_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 674 | [DFR031]BLTHOL_AxU1Left_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 675 | [DFR031]BLTHOL_AxU1Left_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 676 | [DFR031]BLTHOL_AxU1Left_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 677 | [DFR031]BLTHOL_AxU1Left_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 678 | [DFR031]BLTHOL_AxU1Left_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 679 | [DFR031]BLTHOL_AxU1Right_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 680 | [DFR031]BLTHOL_AxU1Right_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 681 | [DFR031]BLTHOL_AxU1Right_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 682 | [DFR031]BLTHOL_AxU1Right_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 683 | [DFR031]BLTHOL_AxU1Right_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 684 | [DFR031]BLTHOL_AxU1Right_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 685 | [DFR031]BLTHOL_AxU2_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 686 | [DFR031]BLTHOL_AxU2_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 687 | [DFR031]BLTHOL_AxU2_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 688 | [DFR031]BLTHOL_AxU2_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 689 | [DFR031]BLTHOL_AxU2_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 690 | [DFR031]BLTHOL_AxU2_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 691 | [DFR031]BLTHOL_U2Track_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 692 | [DFR031]BLTHOL_U2Track_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 693 | [DFR031]BLTHOL_U2Track_ErrIface.b_BltEdgeSensorFault | 1 | 10.168.100.32 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
[8 empty] | 694 | [DFR031]BLTHOL_U2Track_ErrIface.b_TrackMotorFault | 1 | 10.168.100.32 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked.
[8 empty] | 695 | [DFR031]BLTHOL_AxU3_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 696 | [DFR031]BLTHOL_AxU3_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 697 | [DFR031]BLTHOL_AxU3_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 698 | [DFR031]BLTHOL_AxU3_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 699 | [DFR031]BLTHOL_AxU3_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 700 | [DFR031]BLTHOL_AxU3_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 701 | [DFR031]BLTHOL_U3Track_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 702 | [DFR031]BLTHOL_U3Track_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 703 | [DFR031]BLTHOL_U3Track_ErrIface.b_BltEdgeSensorFault | 1 | 10.168.100.32 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
[8 empty] | 704 | [DFR031]BLTHOL_U3Track_ErrIface.b_TrackMotorFault | 1 | 10.168.100.32 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked.
[8 empty] | 705 | [DFR031]BLTHOL_AxU4_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 706 | [DFR031]BLTHOL_AxU4_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 707 | [DFR031]BLTHOL_AxU4_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 708 | [DFR031]BLTHOL_AxU4_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 709 | [DFR031]BLTHOL_AxU4_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 710 | [DFR031]BLTHOL_AxU4_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 711 | [DFR031]BLTHOL_U4Track_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 712 | [DFR031]BLTHOL_U4Track_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 713 | [DFR031]BLTHOL_U4Track_ErrIface.b_BltEdgeSensorFault | 1 | 10.168.100.32 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
[8 empty] | 714 | [DFR031]BLTHOL_U4Track_ErrIface.b_TrackMotorFault | 1 | 10.168.100.32 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked.
[8 empty] | 715 | [DFR031]BLTHOL_AxDdu1_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 716 | [DFR031]BLTHOL_AxDdu1_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 717 | [DFR031]BLTHOL_AxDdu1_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 718 | [DFR031]BLTHOL_AxDdu1_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 719 | [DFR031]BLTHOL_AxDdu1_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 720 | [DFR031]BLTHOL_AxDdu1_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 721 | [DFR031]BLTHOL_Ddu1Track_ErrIface.b_OutOfRange | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 722 | [DFR031]BLTHOL_Ddu1Track_ErrIface.b_OutOfRangeWarn | 1 | 10.168.100.32 | Out of range | The system is unable to correct the tracking of the belt to the specified tolerance.
[8 empty] | 723 | [DFR031]BLTHOL_Ddu1Track_ErrIface.b_BltEdgeSensorFault | 1 | 10.168.100.32 | Belt edge sensor fault | This fault can have several causes. 1. The belt edge sensor is not connected or defective. 2. The belt edge shoe is slipped from the belt.
[8 empty] | 724 | [DFR031]BLTHOL_Ddu1Track_ErrIface.b_TrackMotorFault | 1 | 10.168.100.32 | Motor sensor or motor fault | This fault can have several causes. 1 .The motor sensor is not connected or defective. 2. The motor is not connected, defective or is mechanically blocked.
[8 empty] | 725 | [DFR031]BLTHOL_AxDdu1Left_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 726 | [DFR031]BLTHOL_AxDdu1Left_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 727 | [DFR031]BLTHOL_AxDdu1Left_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 728 | [DFR031]BLTHOL_AxDdu1Left_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 729 | [DFR031]BLTHOL_AxDdu1Left_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 730 | [DFR031]BLTHOL_AxDdu1Left_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 731 | [DFR031]BLTHOL_AxDdu1Right_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 732 | [DFR031]BLTHOL_AxDdu1Right_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 733 | [DFR031]BLTHOL_AxDdu1Right_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 734 | [DFR031]BLTHOL_AxDdu1Right_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 735 | [DFR031]BLTHOL_AxDdu1Right_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 736 | [DFR031]BLTHOL_AxDdu1Right_ErrIface.b_UnitOnBeltNotReady | 1 | 10.168.100.32 | An element on belt is not ready. | A unit on this belt is not ready, therefore it is not possible to run the belt in production.
[8 empty] | 737 | [DFR031]BLTHOL_AxDdu1Ev_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | There is a fault on this drive.
[8 empty] | 738 | [DFR031]BLTHOL_AxDdu1Ev_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 739 | [DFR031]BLTHOL_AxDdu1Ev_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 740 | [DFR031]BLTHOL_AxDdu1Ev_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 741 | [DFR031]BLTHOL_AxDdu1Ev_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 742 | [DFR031]DDU1_SM_ErrIface.b_StateTimeout | 1 | 10.168.100.32 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
[8 empty] | 743 | [DFR031]DDU1_SM_ErrIface.b_ServiceModeActive | 1 | 10.168.100.32 | Service mode active | The unit is in service mode. No production active.
[8 empty] | 744 | [DFR031]DDU1_SM_ErrIface.b_CalculationActive | 1 | 10.168.100.32 | Calculation active | The unit is in calculation state.
[8 empty] | 745 | [DFR031]DDU1_SM_ErrIface.b_StateMachineDisabled | 1 | 10.168.100.32 | Unit switched off | The unit is disabled.
[8 empty] | 746 | [DFR031]DDU1_SM_ErrIface.b_ActivatingPwrFault | 1 | 10.168.100.32 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
[8 empty] | 747 | [DFR031]SFT_DDU1_Saf_ErrIface.CoverLeft.b_DeEnergized | 1 | 10.168.100.32 | Door open left | There is a guard on the machine which is open.
[8 empty] | 748 | [DFR031]SFT_DDU1_Saf_ErrIface.CoverRight.b_DeEnergized | 1 | 10.168.100.32 | Door open right | There is a guard on the machine which is open.
[8 empty] | 749 | [DFR031]DDU1_Saf_ErrIface.b_CoverOpenRequested | 1 | 10.168.100.32 | Doors open requested | The guard will be opened as soon as the last move is done.
[8 empty] | 750 | [DFR031]SFT_DDU1_Saf_ErrIface.EnergizeDrives.b_DeEnergized | 1 | 10.168.100.32 | Energize drives fault | The energizing of the drive is faulted.
[8 empty] | 751 | [DFR031]DDU1_Saf_ErrIface.b_ExhaustValveFault | 1 | 10.168.100.32 | Exhaust valve fault | The exhaust valve has a fault.
[8 empty] | 752 | [DFR031]DDU1_Saf_ErrIface.b_RestartingExhaustValve | 1 | 10.168.100.32 | Restarting exhaust valve | The exhaust valve is restarting.
[8 empty] | 753 | [DFR031]SFT_DDU1_Saf_ErrIface.EnergizeExhaustValve.b_DeEnergized | 1 | 10.168.100.32 | Energize exhaust valve fault | The energizing of the valve is faulted.
[8 empty] | 754 | [DFR031]DDU1_Saf_ErrIface.b_NoCompAir | 1 | 10.168.100.32 | Air pressure too low | The air pressure is below the allowed operating level.
[8 empty] | 755 | [DFR031]DDU1_Saf_ErrIface.b_CompAirNotExhausted | 1 | 10.168.100.32 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
[8 empty] | 756 | [DFR031]DDU1_Ctr_ErrIface.b_LsDistTooSmall | 1 | 10.168.100.32 | Distance Photoeye to belt end to small | The sensor has to be at least 2 minimum gaps plus a maximum row length away from the belt end.
[8 empty] | 757 | [DFR031]DDU1_Ctr_ErrIface.b_HomeNeeded | 1 | 10.168.100.32 | Dump unit home needed | The dump unit is stopping to home after restart.
[8 empty] | 758 | [DFR031]DDU1_Ctr_ErrIface.b_ManualDump | 1 | 10.168.100.32 | Manual dumping active | The manual dumping is active.
[8 empty] | 759 | [DFR031]DDU1_Ctr_ErrIface.b_RemoveProduct | 1 | 10.168.100.32 | Remove all rows from diverter head | After emergency stop or fault, all products have to be removed from the diverter head. Opening and closing the guard of the unit when removing the products will automatically reset this message.
[8 empty] | 760 | [DFR031]DDU1_Ctr_ErrIface.b_MaxPosStopTime | 1 | 10.168.100.32 | Maximum position stop time reached | There was a command to the unit to reach the positioned stop, but the unit needed too long time for this cycle stop. The axis had to stop too fast.
[8 empty] | 761 | [DFR031]DDU1_Ctr_ErrIface.b_CameraNotReady | 1 | 10.168.100.32 | Vision camera not ready | Vision camera is not ready.
[8 empty] | 762 | [DFR031]DDU1_Ctr_ErrIface.b_DownloadActive | 1 | 10.168.100.32 | Data transfer active | Data is being sent to the controller. This message will disappear automatically.
[8 empty] | 763 | [DFR031]DDU1_Ctr_ErrIface.b_TooManyRowsInReg | 1 | 10.168.100.32 | Too many rows in register | There are too many rows between the photoeye and the move position of the diverter.
[8 empty] | 764 | [DFR031]DDU1_Ctr_ErrIface.b_TooManyRowsInReg | 1 | 10.168.100.32 | Too many rows in register | There are too many rows between the photoeye and the move position of the pullnose.
[8 empty] | 765 | [DFR031]DDU1_Ctr_ErrIface.b_CheckPhotoeye | 1 | 10.168.100.32 | Photoeye row detection not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
[8 empty] | 766 | [DFR031]DDU1_Ctr_ErrIface.b_CheckPhotoeyeTooHigh | 1 | 10.168.100.32 | Photoeye too high not ok | Something with this photoeye is not ok (flickering, sees no product, ...). The line will not stop because of this.
[8 empty] | 767 | [DFR031]DDU1_Ctr_ErrIface.b_RowSim | 1 | 10.168.100.32 | Row simulation active | The normal product detection by photo eye has been overridden by the maintenance switch on the touch screen. The element follows a virtual product simulation at a selectable speed.
[8 empty] | 768 | [DFR031]DDU1_Ctr_ErrIface.b_DivrPosNotValid | 1 | 10.168.100.32 | Diverter invalid position parameter | The distance between the dump- and the pass position is more than 180 degrees.
[8 empty] | 769 | [DFR031]DDU1_Ctr_ErrIface.b_PulnPosNotValid | 1 | 10.168.100.32 | Pullnose invalid position parameter | The distance between the open- and the close position is more than 180 degrees.
[8 empty] | 770 | [DFR031]DDU1_Ctr_ErrIface.b_PulnOpenSpdProfileNotValid | 1 | 10.168.100.32 | Pullnose open speed profile not valid | Acceleration and deceleration to open the pullnose are too low or the speed is less than the speed of the belt.
[8 empty] | 771 | [DFR031]DDU1_Ctr_ErrIface.b_PulnCloseSpdProfileNotValid | 1 | 10.168.100.32 | Pullnose close speed profile not valid | Parameter for maximum speed or calculated speed to close the pullnose is less than the belt speed or the calculated deceleration is too high.
[8 empty] | 772 | [DFR031]DDU1_Ctr_ErrIface.b_MDNotReady | 1 | 10.168.100.32 | Metaldetector not ready | The metaldetector which is usually required to operate the system under normal circumstances is not ready (initalization active, faulty or turned off locally).
[8 empty] | 773 | [DFR031]DDU1_Ctr_ErrIface.b_MDOverload | 1 | 10.168.100.32 | Metaldetector overload | Overload metaldetector.
[8 empty] | 774 | [DFR031]DDU1_AxDivr_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
[8 empty] | 775 | [DFR031]DDU1_AxDivr_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 776 | [DFR031]DDU1_AxDivr_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 777 | [DFR031]DDU1_AxDivr_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 778 | [DFR031]DDU1_AxDivr_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 779 | [DFR031]DDU1_AxDivr_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
[8 empty] | 780 | [DFR031]DDU1_AxDivr_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.
[8 empty] | 781 | [DFR031]DDU1_AxPuln_ErrIface.b_DriveFault | 1 | 10.168.100.32 | Drive fault | The drive controller of this motor is reporting a fault condition.
[8 empty] | 782 | [DFR031]DDU1_AxPuln_ErrIface.b_PosErrorFault | 1 | 10.168.100.32 | Position error | The controlled motor is out of the commanded position.
[8 empty] | 783 | [DFR031]DDU1_AxPuln_ErrIface.b_ServoOutputTooHigh | 1 | 10.168.100.32 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
[8 empty] | 784 | [DFR031]DDU1_AxPuln_ErrIface.b_ValidationFault | 1 | 10.168.100.32 | Validation fault | The module detected a drive specific value out of range. Acceleration / deceleration, Speed at 10VDC, ect.
[8 empty] | 785 | [DFR031]DDU1_AxPuln_ErrIface.b_SwitchedOff | 1 | 10.168.100.32 | Switched off | One motor which is usually required to operate the machine under normal circumstances is disabled or turned off.
[8 empty] | 786 | [DFR031]DDU1_AxPuln_ErrIface.b_HomeError | 1 | 10.168.100.32 | Homing not possible | The motors of the machine cannot be synchronized in the set time limit.
[8 empty] | 787 | [DFR031]DDU1_AxPuln_ErrIface.b_CmdMoveError | 1 | 10.168.100.32 | Motion command error | There was a timeout when moving the axis. The motion command could not be completed.

## Alpha HCM 273
HMI Fault Messages:
# | Component | Fault Value | Error Text | Description
1 | PLC1/SMCtr | 1001000 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
2 | PLC1/SMCtr | 1001001 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
3 | PLC1/SMCtr | 1001002 | Too small | This is a system failure: the shown registration list is too small.
4 | PLC1/SMCtr | 1001003 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
5 | PLC1/SMCtr | 1001004 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
6 | PLC1/SMCtr | 1001005 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
7 | PLC1/SMCtr | 1001006 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
8 | PLC1/SMCtr | 1001007 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
9 | PLC1/SMCtr | 1001008 | Controller Timeout | Global Statemachine fault.
10 | PLC1/SMCtr | 1001009 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
11 | PLC1/SMCtr | 1001010 | State machine init - | This is a system failure.
12 | PLC1/SMCtr | 1001011 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
13 | HMI | 1002000 | Product setup download active | There was a request for a format download job, but the download is not finished yet.
14 | PLC1/CPU | 1003000 | Battery low | The voltage of the internal battery of the PLC is low.
15 | PLC1/CPU | 1003003 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout.
16 | GMS | 1004000 | Power supply 24 V DC | The 24 V DC power supply is not ok.
17 | GMS | 1004001 | Circuit breaker solenoids power | The circuit breaker for the solenoids power is switched off. This circuit is used basically for solenoids opening and closing longitudinal sealing rolls and splicer.
18 | GMS | 1004002 | Air pressure too low | The air pressure is below the allowed operating level.
19 | GMS | 1004003 | Circuit breaker CAB2 power | The circuit breaker is turned off.
20 | GMS | 1004004 | Circuit breaker CAB2 control power | The circuit breaker is turned off.
21 | GMS | 1004005 | Circuit breaker transformer sealing | The circuit breaker before the transformer for the sealing equipment is switched off.
22 | GMS | 1004006 | Circuit breaker CAB1 power | The circuit breaker is turned off.
23 | GMS | 1004010 | Aircondition unit CAB 1 message | The aircondition unit has an active message.
24 | GMS | 1004011 | Circuit breaker aircondition unit CAB 1 | The residual current circuit breaker for the aircondition unit is turned off.
25 | GMS | 1004012 | Aircondition unit CAB 2 message | The aircondition unit has an active message.
26 | GMS | 1004013 | Circuit breaker aircondition unit CAB 2 | The residual current circuit breaker for the aircondition unit is turned off.
27 | GMS | 1004020 | Circuit breaker Kinetix rack 1 | The circuit breaker is switched off.
28 | GMS | 1004021 | Circuit breaker control power Kinetix rack 1 | The circuit breaker is switched off.
29 | GMS | 1004022 | Circuit breaker Kinetix rack 2 | The circuit breaker is switched off.
30 | GMS | 1004023 | Circuit breaker control power Kinetix rack 2 | The circuit breaker is switched off.
31 | GMS | 1004024 | Circuit breaker Kinetix rack 3 | The circuit breaker is switched off.
32 | GMS | 1004025 | Circuit breaker control power Kinetix rack 3 | The circuit breaker is switched off.
33 | GMS | 1004026 | Circuit breaker Kinetix rack 4 | The circuit breaker is switched off.
34 | GMS | 1004027 | Circuit breaker control power Kinetix rack 4 | The circuit breaker is switched off.
35 | GMS | 1004028 | Circuit breaker Kinetix rack 5 | The circuit breaker is switched off.
36 | GMS | 1004029 | Circuit breaker control power Kinetix rack 5 | The circuit breaker is switched off.
37 | GMS | 1004040 | Circuit breaker power supply ultra sonic generator | The circuit breaker is switched off.
38 | PLC1/IO | 1005001 | Electronic fuse triggered on 2A digital output card | The electronic protection circuit of one the of digital output cards for 2A high power outputs of the PLC has been activated due to a short circuit.
39 | PLC1/IO | 1005002 | Missing remote I/O rack 00 | One of the Remote I/O modules is missing.
40 | PLC1/IO | 1005003 | Missing remote I/O rack 01 | One of the Remote I/O modules is missing.
41 | PLC1/IO | 1005004 | Missing remote I/O rack 02 | One of the Remote I/O modules is missing.
42 | PLC1/IO | 1005005 | Missing remote I/O rack 03 | One of the Remote I/O modules is missing.
43 | SAF1 | 1021006 | LOTO switch main cabinet turned off | The Lock Out Tag Out (LOTO) switch at main cabinet is turned off.
44 | SAF1 | 1021011 | Emergency stop machine | The emergency stop button is pressed or has already been disengaged.
45 | SAF1 | 1021013 | Emergency stop cardboard feeder | The emergency stop button is pressed or has already been disengaged.
46 | SAF1 | 1021015 | Emergency stop control belt | The emergency stop button is pressed or has already been disengaged.
47 | SAF1 | 1021016 | Emergency stop alignment belt | The emergency stop button is pressed or has already been disengaged.
48 | SAF1 | 1021017 | Emergency stop turning belts | The emergency stop button is pressed or has already been disengaged.
49 | SAF1 | 1021019 | Emergency stop distribution unit | The emergency stop button is pressed or has already been disengaged.
50 | SAF1 | 1021021 | Emergency stop infeed transport belts | The emergency stop button is pressed or has already been disengaged.
51 | SAF1 | 1021070 | Emergency stop feeding wheel front side | The emergency stop button is pressed or has already been disengaged.
52 | SAF1 | 1021071 | Emergency stop feeding wheel rear side | The emergency stop button is pressed or has already been disengaged.
53 | SAF1 | 1021072 | Emergency stop feeding wheel infeed | The emergency stop button is pressed or has already been disengaged.
54 | SAF1 | 1021073 | Emergency stop feeding wheel outfeed | The emergency stop button is pressed or has already been disengaged.
55 | SAF1 | 1021079 | Emergency stop customer | The emergency stop button from an other machine is pressed.
56 | SAF1 | 1021080 | Energize drives vacuum pump outfeed belt fault | The energizing of the drives is faulted.
57 | SAF1 | 1021081 | Energize vacuum pump metering belt fault | The energizing of the vacuum pump is faulted.
58 | SAF1 | 1021082 | Energize empty pack suction fault | The energizing of the vacuum pump is faulted.
59 | SAF1 | 1021083 | Energize vacuum pump longitudinal fault | The energizing of the vacuum pump is faulted.
60 | SAF1 | 1021084 | Energize drives longitudinal vacuum pump fault | The energizing of the drives is faulted.
61 | SAF1 | 1021085 | Energize drives empty pack suction fault | The energizing of the drives is faulted.
62 | SAF1 | 1021090 | Exhaust valve fault | The exhaust valve has a fault.
63 | SAF1 | 1021091 | Restarting exhaust valve | The exhaust valve is restarting.
64 | SAF1 | 1021092 | Energize exhaust valve fault | The energizing of the valve is faulted.
65 | SAF1 | 1021093 | Air pressure too low | The air pressure is below the allowed operating level.
66 | SAF1 | 1021094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
67 | PLC1/STA | 1051001 | No SD card | The SD card in the controller is missing
68 | PLC1/STA | 1051002 | SD card write error | The Prozessor has a problem to write the datas to the SD card
69 | PLC1/STA | 1051003 | SD card read error | The Prozessor has a problem to read the datas from the SD card
70 | PLC2/SMCtr | 2001000 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
71 | PLC2/SMCtr | 2001001 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
72 | PLC2/SMCtr | 2001002 | Too small | This is a system failure: the shown registration list is too small.
73 | PLC2/SMCtr | 2001003 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
74 | PLC2/SMCtr | 2001004 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
75 | PLC2/SMCtr | 2001005 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
76 | PLC2/SMCtr | 2001006 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
77 | PLC2/SMCtr | 2001007 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
78 | PLC2/SMCtr | 2001008 | Controller Timeout | Global Statemachine fault.
79 | PLC2/SMCtr | 2001009 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
80 | PLC2/SMCtr | 2001010 | State machine init - | This is a system failure.
81 | PLC2/SMCtr | 2001011 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
82 | PLC2/CPU | 2003000 | Battery low | The voltage of the internal battery of the PLC is low.
83 | PLC2/CPU | 2003003 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout.
84 | PLC2/CPU | 2003010 | Please open the safety circuit | For the update of a conversion constante of a consumed axis is an open safety circuit required. Pleace open a guard or press the emergency stop.
85 | PLC2/IO | 2005001 | Electronic fuse triggered on 2A digital output card | The electronic protection circuit of one the of digital output cards for 2A high power outputs of the PLC has been activated due to a short circuit.
86 | PLC2/IO | 2005002 | Missing remote I/O rack 00 | One of the Remote I/O modules is missing.
87 | PLC2/IO | 2005003 | Missing remote I/O rack 01 | One of the Remote I/O modules is missing.
88 | PLC2/IO | 2005004 | Missing remote I/O rack 02 | One of the Remote I/O modules is missing.
89 | PLC2/IO | 2005005 | Missing remote I/O rack 03 | One of the Remote I/O modules is missing.
90 | PLC2/STA | 2051001 | No SD card | The SD card in the controller is missing
91 | PLC2/STA | 2051002 | SD card write error | The Prozessor has a problem to write the datas to the SD card
92 | PLC2/STA | 2051003 | SD card read error | The Prozessor has a problem to read the datas from the SD card
93 | FXX1/SM | 51010000 | State timeout | This is a system failure of this unit. There was a timeout in a state that needed to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
94 | FXX1/SM | 51010002 | Calculation active | There was a request for a calculation job, but the calculation is not finished yet.
95 | FXX1/SM | 51010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
96 | FXX1 | 51012000 | A feeding part is not homed | The home procedure has not been carried out yet.
97 | FXX1 | 51012001 | Feeder is homing | The feeding system is homing or synchronising
98 | FXX1/Speed Nose | 51060001 | Validation fault | Validation fault of the speed module "nose".
99 | FXX1/Speed | 51060002 | Sensor plus correction not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
100 | FXX1/Speed | 51060003 | Sensor minus correction not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
101 | FXX1/Speed | 51060004 | Overflow at infeed | The proportional photoeye did not detect any gap for a few products.
102 | FXX1/Speed | 51060005 | Check proportional photoeye | The photoeye detecting the incoming product has seen too many too small products.
103 | FXX1/Speed | 51060006 | Sensor proportional photoeye not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
104 | FXX1/Speed | 51060010 | Production stopped - infeed belts stopped | The belts stopped because there was no product coming in for a certain time.
105 | FXX1/TranspBelt1 | 51201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
106 | FXX1/TranspBelt1 | 51201001 | Position error | The controlled motor is out of the commanded position.
107 | FXX1/TranspBelt1 | 51201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
108 | FXX1/TranspBelt1 | 51201003 | Validation fault | The module detected a value out of range.
109 | FXX1/TranspBelt1 | 51201004 | Switched off | The motor has been switched off temporarily.
110 | FXX1/TranspBelt2 | 51202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
111 | FXX1/TranspBelt2 | 51202001 | Position error | The controlled motor is out of the commanded position.
112 | FXX1/TranspBelt2 | 51202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
113 | FXX1/TranspBelt2 | 51202003 | Validation fault | The module detected a value out of range.
114 | FXX1/TranspBelt2 | 51202004 | Switched off | The motor has been switched off temporarily.
115 | FXX1/TranspBelt3 | 51203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
116 | FXX1/TranspBelt3 | 51203001 | Position error | The controlled motor is out of the commanded position.
117 | FXX1/TranspBelt3 | 51203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
118 | FXX1/TranspBelt3 | 51203003 | Validation fault | The module detected a value out of range.
119 | FXX1/TranspBelt3 | 51203004 | Switched off | The motor has been switched off temporarily.
120 | FXX1/TurnBeltFront | 51221000 | Drive fault | The drive controller of this motor is reporting a fault condition.
121 | FXX1/TurnBeltFront | 51221001 | Position error | The controlled motor is out of the commanded position.
122 | FXX1/TurnBeltFront | 51221002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
123 | FXX1/TurnBeltFront | 51221003 | Validation fault | The module detected a value out of range.
124 | FXX1/TurnBeltFront | 51221004 | Switched off | The motor has been switched off temporarily.
125 | FXX1/TurnBeltRear | 51222000 | Drive fault | The drive controller of this motor is reporting a fault condition.
126 | FXX1/TurnBeltRear | 51222001 | Position error | The controlled motor is out of the commanded position.
127 | FXX1/TurnBeltRear | 51222002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
128 | FXX1/TurnBeltRear | 51222003 | Validation fault | The module detected a value out of range.
129 | FXX1/TurnBeltRear | 51222004 | Switched off | The motor has been switched off temporarily.
130 | FXX1/TurnBeltAcc | 51223000 | Drive fault | The drive controller of this motor is reporting a fault condition.
131 | FXX1/TurnBeltAcc | 51223001 | Position error | The controlled motor is out of the commanded position.
132 | FXX1/TurnBeltAcc | 51223002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
133 | FXX1/TurnBeltAcc | 51223003 | Validation fault | The module detected a value out of range.
134 | FXX1/TurnBeltAcc | 51223004 | Switched off | The motor has been switched off temporarily.
135 | FXX1/AlignBelt | 51224000 | Drive fault | The drive controller of this motor is reporting a fault condition.
136 | FXX1/AlignBelt | 51224001 | Position error | The controlled motor is out of the commanded position.
137 | FXX1/AlignBelt | 51224002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
138 | FXX1/AlignBelt | 51224003 | Validation fault | The module detected a value out of range.
139 | FXX1/AlignBelt | 51224004 | Switched off | The motor has been switched off temporarily.
140 | FXX1/AlignSideBelt | 51225000 | Drive fault | The drive controller of this motor is reporting a fault condition.
141 | FXX1/AlignSideBelt | 51225001 | Position error | The controlled motor is out of the commanded position.
142 | FXX1/AlignSideBelt | 51225002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
143 | FXX1/AlignSideBelt | 51225003 | Validation fault | The module detected a value out of range.
144 | FXX1/AlignSideBelt | 51225004 | Switched off | The motor has been switched off temporarily.
145 | FXX1/ControlBelt | 51226000 | Drive fault | The drive controller of this motor is reporting a fault condition.
146 | FXX1/ControlBelt | 51226001 | Position error | The controlled motor is out of the commanded position.
147 | FXX1/ControlBelt | 51226002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
148 | FXX1/ControlBelt | 51226003 | Validation fault | The module detected a value out of range.
149 | FXX1/ControlBelt | 51226004 | Switched off | The motor has been switched off temporarily.
150 | FXX1/ControlBelt2 | 51227000 | Drive fault | The drive controller of this motor is reporting a fault condition.
151 | FXX1/ControlBelt2 | 51227001 | Position error | The controlled motor is out of the commanded position.
152 | FXX1/ControlBelt2 | 51227002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
153 | FXX1/ControlBelt2 | 51227003 | Validation fault | The module detected a value out of range.
154 | FXX1/ControlBelt2 | 51227004 | Switched off | The motor has been switched off temporarily.
155 | FXX1/ControlBelt2 | 51227011 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
156 | FXX1/ControlBelt3 | 51228000 | Drive fault | The drive controller of this motor is reporting a fault condition.
157 | FXX1/ControlBelt3 | 51228001 | Position error | The controlled motor is out of the commanded position.
158 | FXX1/ControlBelt3 | 51228002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
159 | FXX1/ControlBelt3 | 51228003 | Validation fault | The module detected a value out of range.
160 | FXX1/ControlBelt3 | 51228004 | Switched off | The motor has been switched off temporarily.
161 | FXX1/ControlBelt3 | 51228011 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
162 | FBP/Nose | 51230000 | Drive fault | The drive controller of this motor is reporting a fault condition.
163 | FBP/Nose | 51230001 | Position error | The controlled motor is out of the commanded position.
164 | FBP/Nose | 51230002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
165 | FBP/Nose | 51230003 | Validation fault | The module detected a value out of range.
166 | FBP/Nose | 51230004 | Switched off | The motor has been switched off temporarily.
167 | FBP/Nose | 51230006 | Proximity switch not found | During hard home procedure the home position could not been detected.
168 | FBP/Nose | 51230008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
169 | FBP/Nose | 51230011 | Negative overtravel | The axis has exceeded the software limit position in negative direction.
170 | FBP/Nose | 51230012 | Positive overtravel | The axis has exceeded the software limit position in positive direction.
171 | FXX1/Jam | 51240000 | Jam at infeed | Product jam at the infeed side of the machine.
172 | FXX1/Jam | 51240001 | Sensor jam at infeed not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
173 | FXX1/MetalDet | 51241000 | Circuit breaker | The circuit breaker for the metal detector is switched off.
174 | FXX1/MetalDet | 51241001 | Not ready | The metal detector is not ready.
175 | FXX1/MetalDet | 51241002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
176 | FXX1/MetalDet | 51241003 | Sensor back not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
177 | FXX1/MetalDet | 51241004 | Sensor verification not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
178 | FXX1/MetalDet | 51241005 | Product not rejected | Products were not rejected
179 | FXX1/MetalDet | 51241006 | Sensor verification back not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
180 | FXX1/MetalDet | 51241007 | Product not rejected back | Products were not rejected
181 | FXX1/3D Check | 51244001 | Sensor length detection not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
182 | FXX1/3D Check | 51244002 | Validation fault | The module detected a value out of range.
183 | HXX/SM | 60010000 | State timeout | This is a system failure of this unit. There was a timeout in a state that needed to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
184 | HXX/SM | 60010002 | Calculation active | There was a request for a calculation job, but the calculation is not finished yet.
185 | HXX/SM | 60010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
186 | HXX | 60012000 | Remove all products from the infeed | Position of the corresponding motor is no more valid.
187 | HXX | 60012001 | Remove all products between machine chain and film | Position of the corresponding motor is no more valid.
188 | HXX | 60012002 | Remove all products from the longitudinal sealing | Position of the corresponding motor is no more valid.
189 | HXX | 60012003 | Remove all products from the cross seal | Position of the corresponding motor is no more valid.
190 | HXX | 60012004 | Remove all products from the machine outfeed belt | Position of the corresponding motor is no more valid.
191 | HXX | 60012005 | Machine is not homed | The home procedure has not been carried out yet.
192 | HXX | 60012006 | Machine is homing | After a size or parameter change the axis will re-home to proximity switches.
193 | HXX | 60012007 | Machine is synchronizing | After an emergency stop or after moving one of the axes manually the axis will move back to the desired position.
194 | HXX | 60012008 | Remove cardboards from the cardboard chain | Remove cardboards from the cardboard chain
195 | HXX | 60050000 | Product dimensions validation fault | The module detected a value out of range.
196 | HXX | 60050002 | Finished emptying | The emptying of the machine is finsihed.
197 | HXX | 60101000 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
198 | HXX/FXXIface | 60105000 | No product at infeed | The machine has stopped because there is no product being fed to it.
199 | HXX/Heater | 60110001 | Circuit breaker | The heater circuit breaker is switched off.
200 | HXX/Heater | 60110002 | Heaters are in warm-up procedure | The heaters are in warm-up procedure.
201 | HXX/Heater | 60110003 | Caution! Heaters are still hot | The heaters have not cooled down yet.
202 | HXX/Heater | 60110004 | Heaters are in warm-up procedure | The heaters are in warm-up procedure.
203 | HXX/Heat Lng2 rear | 60111000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
204 | HXX/Heat Lng2 rear | 60111001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
205 | HXX/Heat Lng2 rear | 60111002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
206 | HXX/Heat Lng2 rear | 60111003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
207 | HXX/Heat Lng2 rear | 60111004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
208 | HXX/Heat Lng2 rear | 60111005 | Heating time too long | This heater needs too long to warm up.
209 | HXX/Heat Lng2 rear | 60111006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
210 | HXX/Heat Lng2 rear | 60111007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
211 | HXX/Heat Lng2 rear | 60111008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
212 | HXX/Heat Lng2 rear | 60111009 | Heating time too long | This heater needs too long to warm up.
213 | HXX/Heat Lng2 front | 60112000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
214 | HXX/Heat Lng2 front | 60112001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
215 | HXX/Heat Lng2 front | 60112002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
216 | HXX/Heat Lng2 front | 60112003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
217 | HXX/Heat Lng2 front | 60112004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
218 | HXX/Heat Lng2 front | 60112005 | Heating time too long | This heater needs too long to warm up.
219 | HXX/Heat Lng2 front | 60112006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
220 | HXX/Heat Lng2 front | 60112007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
221 | HXX/Heat Lng2 front | 60112008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
222 | HXX/Heat Lng2 front | 60112009 | Heating time too long | This heater needs too long to warm up.
223 | HXX/Heat Lng3 rear | 60113000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
224 | HXX/Heat Lng3 rear | 60113001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
225 | HXX/Heat Lng3 rear | 60113002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
226 | HXX/Heat Lng3 rear | 60113003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
227 | HXX/Heat Lng3 rear | 60113004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
228 | HXX/Heat Lng3 rear | 60113005 | Heating time too long | This heater needs too long to warm up.
229 | HXX/Heat Lng3 rear | 60113006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
230 | HXX/Heat Lng3 rear | 60113007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
231 | HXX/Heat Lng3 rear | 60113008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
232 | HXX/Heat Lng3 rear | 60113009 | Heating time too long | This heater needs too long to warm up.
233 | HXX/Heat Lng3 front | 60114000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
234 | HXX/Heat Lng3 front | 60114001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
235 | HXX/Heat Lng3 front | 60114002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
236 | HXX/Heat Lng3 front | 60114003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
237 | HXX/Heat Lng3 front | 60114004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
238 | HXX/Heat Lng3 front | 60114005 | Heating time too long | This heater needs too long to warm up.
239 | HXX/Heat Lng3 front | 60114006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
240 | HXX/Heat Lng3 front | 60114007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
241 | HXX/Heat Lng3 front | 60114008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
242 | HXX/Heat Lng3 front | 60114009 | Heating time too long | This heater needs too long to warm up.
243 | HXX/Heat Crs up1 | 60115000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
244 | HXX/Heat Crs up1 | 60115001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
245 | HXX/Heat Crs up1 | 60115002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
246 | HXX/Heat Crs up1 | 60115003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
247 | HXX/Heat Crs up1 | 60115004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
248 | HXX/Heat Crs up1 | 60115005 | Heating time too long | This heater needs too long to warm up.
249 | HXX/Heat Crs up1 | 60115006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
250 | HXX/Heat Crs up1 | 60115007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
251 | HXX/Heat Crs up1 | 60115008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
252 | HXX/Heat Crs up1 | 60115009 | Heating time too long | This heater needs too long to warm up.
253 | HXX/Heat Crs up2 | 60116000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
254 | HXX/Heat Crs up2 | 60116001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
255 | HXX/Heat Crs up2 | 60116002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
256 | HXX/Heat Crs up2 | 60116003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
257 | HXX/Heat Crs up2 | 60116004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
258 | HXX/Heat Crs up2 | 60116005 | Heating time too long | This heater needs too long to warm up.
259 | HXX/Heat Crs up2 | 60116006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
260 | HXX/Heat Crs up2 | 60116007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
261 | HXX/Heat Crs up2 | 60116008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
262 | HXX/Heat Crs up2 | 60116009 | Heating time too long | This heater needs too long to warm up.
263 | HXX/Heat Crs low1 | 60118000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
264 | HXX/Heat Crs low1 | 60118001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
265 | HXX/Heat Crs low1 | 60118002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
266 | HXX/Heat Crs low1 | 60118003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
267 | HXX/Heat Crs low1 | 60118004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
268 | HXX/Heat Crs low1 | 60118005 | Heating time too long | This heater needs too long to warm up.
269 | HXX/Heat Crs low1 | 60118006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
270 | HXX/Heat Crs low1 | 60118007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
271 | HXX/Heat Crs low1 | 60118008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
272 | HXX/Heat Crs low1 | 60118009 | Heating time too long | This heater needs too long to warm up.
273 | HXX/Heat Crs low2 | 60119000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
274 | HXX/Heat Crs low2 | 60119001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
275 | HXX/Heat Crs low2 | 60119002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
276 | HXX/Heat Crs low2 | 60119003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
277 | HXX/Heat Crs low2 | 60119004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
278 | HXX/Heat Crs low2 | 60119005 | Heating time too long | This heater needs too long to warm up.
279 | HXX/Heat Crs low2 | 60119006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
280 | HXX/Heat Crs low2 | 60119007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
281 | HXX/Heat Crs low2 | 60119008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
282 | HXX/Heat Crs low2 | 60119009 | Heating time too long | This heater needs too long to warm up.
283 | HXX/PreHeat rear | 60121000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
284 | HXX/PreHeat rear | 60121001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
285 | HXX/PreHeat rear | 60121002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
286 | HXX/PreHeat rear | 60121003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
287 | HXX/PreHeat rear | 60121004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
288 | HXX/PreHeat rear | 60121005 | Heating time too long | This heater needs too long to warm up.
289 | HXX/PreHeat rear | 60121006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
290 | HXX/PreHeat rear | 60121007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
291 | HXX/PreHeat rear | 60121008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
292 | HXX/PreHeat rear | 60121009 | Heating time too long | This heater needs too long to warm up.
293 | HXX/PreHeat front | 60122000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
294 | HXX/PreHeat front | 60122001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
295 | HXX/PreHeat front | 60122002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
296 | HXX/PreHeat front | 60122003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
297 | HXX/PreHeat front | 60122004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
298 | HXX/PreHeat front | 60122005 | Heating time too long | This heater needs too long to warm up.
299 | HXX/PreHeat front | 60122006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
300 | HXX/PreHeat front | 60122007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
301 | HXX/PreHeat front | 60122008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
302 | HXX/PreHeat front | 60122009 | Heating time too long | This heater needs too long to warm up.
303 | HXX/MetBeltVac | 60140000 | Circuit breaker | The circuit breaker is switched off.
304 | HXX/MetBeltVac | 60140001 | Waiting for vacuum | The vacuum pump is starting up.
305 | HXX/OutfVacEmpty | 60141000 | Circuit breaker | The circuit breaker is switched off.
306 | HXX/OutfVacEmpty | 60141001 | Waiting for vacuum | The vacuum pump is starting up.
307 | HXX/OutfVacEmpty | 60141002 | Drive fault | The drive controller of this motor is reporting a fault condition.
308 | HXX/OutfVacEmpty | 60141003 | Validation fault | The module detected a value out of range.
309 | HXX/OutfVacEmpty | 60141005 | Empty wrap vacuum isolater disconneted | The motor has been disconnected.
310 | HXX/SensorTeach | 60150000 | Sensor teaching is active | The sensor teaching ist active.
311 | HXX/VAxMaster | 60200008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
312 | HXX/VAxMaster | 60200010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
313 | HXX/VAxMaster | 60200012 | External speed too high | The speed of the external master axis is higher than maximum speed.
314 | HXX/NPNP | 60201008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
315 | HXX/NPNP | 60201010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
316 | HXX/Film | 60202008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
317 | HXX/Film | 60202010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
318 | HXX/NGNS | 60203008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
319 | HXX/NGNS | 60203010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
320 | HXX/VAxOutfBelt | 60204008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
321 | HXX/VAxOutfBelt | 60204010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
322 | HXX/OutfBelt | 60210001 | Position error | The controlled motor is out of the commanded position.
323 | HXX/OutfBelt | 60210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
324 | HXX/OutfBelt | 60210003 | Validation fault | The module detected a value out of range.
325 | HXX/OutfBelt | 60210004 | Switched off | The motor has been switched off temporarily.
326 | HXX/OutfBelt | 60210008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
327 | HXX/OutfBelt | 60210010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
328 | HXX/Crs | 60211000 | Drive fault | The drive controller of this motor is reporting a fault condition.
329 | HXX/Crs | 60211001 | Position error | The controlled motor is out of the commanded position.
330 | HXX/Crs | 60211002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
331 | HXX/Crs | 60211003 | Validation fault | The module detected a value out of range.
332 | HXX/Crs | 60211004 | Switched off | The motor has been switched off temporarily.
333 | HXX/Crs | 60211006 | Proximity switch not found | During hard home procedure the home position could not been detected.
334 | HXX/Crs | 60211007 | Motor brake manually released | The electrical brake of the cross seal motor is manually released.
335 | HXX/Crs | 60211008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
336 | HXX/Crs | 60211010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
337 | HXX/Lng1 | 60212000 | Drive fault | The drive controller of this motor is reporting a fault condition.
338 | HXX/Lng1 | 60212001 | Position error | The controlled motor is out of the commanded position.
339 | HXX/Lng1 | 60212002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
340 | HXX/Lng1 | 60212003 | Validation fault | The module detected a value out of range.
341 | HXX/Lng1 | 60212004 | Switched off | The motor has been switched off temporarily.
342 | HXX/Lng1 | 60212005 | Film home selected | A film home has been selected or the film is out of synchronization.
343 | HXX/Lng1 | 60212008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
344 | HXX/Lng1 | 60212010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
345 | HXX/Lng1 | 60212011 | Bad registration marks detected | A consecutive number of marks or flickers have been out of position. This could either mean that there are too many marks or that the sensor is flickering.
346 | HXX/Lng1 | 60212012 | Registration mark not detected | The registration sensor did not see any registration mark for several cycles.
347 | HXX/Lng1 | 60212013 | Film registration error | The machine is unable to correct the registration to the specified tolerance.
348 | HXX/FilmFeeder | 60213000 | Drive fault | The drive controller of this motor is reporting a fault condition.
349 | HXX/FilmFeeder | 60213001 | Position error | The controlled motor is out of the commanded position.
350 | HXX/FilmFeeder | 60213002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
351 | HXX/FilmFeeder | 60213003 | Validation fault | The module detected a value out of range.
352 | HXX/FilmFeeder | 60213004 | Switched off | The motor has been switched off temporarily.
353 | HXX/FilmFeeder | 60213008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
354 | HXX/FilmFeeder | 60213010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
355 | HXX/InfChain | 60214000 | Drive fault | The drive controller of this motor is reporting a fault condition.
356 | HXX/InfChain | 60214001 | Position error | The controlled motor is out of the commanded position.
357 | HXX/InfChain | 60214002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
358 | HXX/InfChain | 60214003 | Validation fault | The module detected a value out of range.
359 | HXX/InfChain | 60214004 | Switched off | The motor has been switched off temporarily.
360 | HXX/InfChain | 60214006 | Proximity switch not found | During hard home procedure the home position could not been detected.
361 | HXX/InfChain | 60214008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
362 | HXX/InfChain | 60214010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
363 | HXX/InfChain | 60214011 | Flight check fault | During the "chain flight check" a chain lug was detected at the wrong position.
364 | HXX/AccBelt | 60215000 | Drive fault | The drive controller of this motor is reporting a fault condition.
365 | HXX/AccBelt | 60215001 | Position error | The controlled motor is out of the commanded position.
366 | HXX/AccBelt | 60215002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
367 | HXX/AccBelt | 60215003 | Validation fault | The module detected a value out of range.
368 | HXX/AccBelt | 60215004 | Switched off | The motor has been switched off temporarily.
369 | HXX/AccBelt | 60215008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
370 | HXX/AccBelt | 60215010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
371 | HXX/MetBelt | 60216000 | Drive fault | The drive controller of this motor is reporting a fault condition.
372 | HXX/MetBelt | 60216001 | Position error | The controlled motor is out of the commanded position.
373 | HXX/MetBelt | 60216002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
374 | HXX/MetBelt | 60216003 | Validation fault | The module detected a value out of range.
375 | HXX/MetBelt | 60216004 | Switched off | The motor has been switched off temporarily.
376 | HXX/MetBelt | 60216008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
377 | HXX/MetBelt | 60216010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
378 | HXX/MetBelt | 60216011 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
379 | HXX/Lng2 | 60222000 | Drive fault | The drive controller of this motor is reporting a fault condition.
380 | HXX/Lng2 | 60222001 | Position error | The controlled motor is out of the commanded position.
381 | HXX/Lng2 | 60222002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
382 | HXX/Lng2 | 60222003 | Validation fault | The module detected a value out of range.
383 | HXX/Lng2 | 60222004 | Switched off | The motor has been switched off temporarily.
384 | HXX/Lng2 | 60222008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
385 | HXX/Lng2 | 60222010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
386 | HXX/AxTopGuideBlt | 60224000 | Drive fault | The drive controller of this motor is reporting a fault condition.
387 | HXX/AxTopGuideBlt | 60224001 | Position error | The controlled motor is out of the commanded position.
388 | HXX/AxTopGuideBlt | 60224002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
389 | HXX/AxTopGuideBlt | 60224003 | Validation fault | The module detected a value out of range.
390 | HXX/AxTopGuideBlt | 60224004 | Switched off | The motor has been switched off temporarily.
391 | HXX/AxTopGuideBlt | 60224010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
392 | HXX/AxTopGuideBlt | 60224011 | Top guide belt not in working position | The top guide belt is not in working position.
393 | HXX/OpenCloseLng | 60230000 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
394 | HXX/LngVac | 60232000 | Drive fault | There is a fault on this drive.
395 | HXX/LngVac | 60232001 | Validation fault | The module detected a value out of range.
396 | HXX/LngVac | 60232002 | Circuit breaker | The circuit breaker for remove air at longitudinal sealing is switched off.
397 | HXX/AccProdInsp | 60255000 | Validation fault | The module detected a value out of range.
398 | HXX/AccProdInsp | 60255001 | Product too long | The product supervision detected a too long product in the infeed chain.
399 | HXX/AccProdInsp | 60255002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
400 | HXX/SRTransf | 60260001 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
401 | HXX/ProdInsp | 60262000 | Validation fault | The module detected a value out of range.
402 | HXX/ProdInsp | 60262001 | Product too long | The product supervision detected a too long product in the infeed chain.
403 | HXX/ProdInsp | 60262002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
404 | HXX/HighInsp | 60263000 | Validation fault | The module detected a value out of range.
405 | HXX/HighInsp | 60263001 | Product too high | The sensor which detects too high products has been activated.
406 | HXX/InfRej | 60264000 | Validation fault | The module detected a value out of range.
407 | HXX/InfRej | 60264001 | Too many products rejected over several cycles | Too many products were rejected continuously over several cycles.
408 | HXX/CrdBrdInsp | 60267000 | Validation fault | The module detected a value out of range.
409 | HXX/CrdBrdInsp | 60267001 | Cardboard too long | A cardboard in the infeed chain is too long or has jammed.
410 | HXX/CrdBrdInsp | 60267002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
411 | HXX/CrdBrdJam | 60268000 | Validation fault | The module detected a value out of range.
412 | HXX/CrdBrdJam | 60268001 | Jam | A cardboard in the infeed chain is too long or has jammed.
413 | HXX/CrdBrdJam | 60268002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
414 | HXX/AxChainSwitch | 60280000 | Drive fault | The drive controller of this motor is reporting a fault condition.
415 | HXX/AxChainSwitch | 60280001 | Position error | The controlled motor is out of the commanded position.
416 | HXX/AxChainSwitch | 60280002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
417 | HXX/AxChainSwitch | 60280003 | Validation fault | The module detected a value out of range.
418 | HXX/AxChainSwitch | 60280004 | Switched off | The motor has been switched off temporarily.
419 | HXX/AxChainSwitch | 60280007 | Brake manually released | The electrical brake of the chain switch motor is manually released.
420 | HXX/AxChainSwitch | 60280008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
421 | HXX/AxChainSwitch | 60280010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
422 | HXX/AxChainSwitch | 60280011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
423 | HXX/InfChain | 60285000 | No signal additional sensor | The additional proximity switch on the infeed chain did not detect any chain lug.
424 | HXX/AxSideGuide1 | 60298000 | Drive fault | The drive controller of this motor is reporting a fault condition.
425 | HXX/AxSideGuide1 | 60298001 | Position error | The controlled motor is out of the commanded position.
426 | HXX/AxSideGuide1 | 60298002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
427 | HXX/AxSideGuide1 | 60298003 | Validation fault | The module detected a value out of range.
428 | HXX/AxSideGuide1 | 60298004 | Switched off | The motor has been switched off temporarily.
429 | HXX/AxSideGuide1 | 60298010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
430 | HXX/AxSideGuide1 | 60298011 | Side guide belt not in working position | The side guide belt is not in working position.
431 | HXX/AxSideGuide2 | 60299000 | Drive fault | The drive controller of this motor is reporting a fault condition.
432 | HXX/AxSideGuide2 | 60299001 | Position error | The controlled motor is out of the commanded position.
433 | HXX/AxSideGuide2 | 60299002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
434 | HXX/AxSideGuide2 | 60299003 | Validation fault | The module detected a value out of range.
435 | HXX/AxSideGuide2 | 60299004 | Switched off | The motor has been switched off temporarily.
436 | HXX/AxSideGuide2 | 60299010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
437 | HXX/AxSideGuide2 | 60299011 | Side guide belt not in working position | The side guide belt is not in working position.
438 | HXX/FilmTrack | 60301000 | Home error | The homing of the film tracking control has not been successful.
439 | HXX/FilmTrack | 60301000 | Home error | The homing of the film tracking control has not been successful.
440 | HXX/FilmTrack | 60301001 | Homing active | The film tracking control is homing.
441 | HXX/FilmTrack | 60301001 | Homing active | The film tracking control is homing.
442 | HXX/FilmTrack | 60301002 | Not ready | The film tracking is not ready.
443 | HXX/FilmTrack | 60301002 | Not ready | The film tracking is not ready.
444 | HXX/FilmTrack | 60301003 | Film out of window | The film is not within the allowed window.
445 | HXX/FilmTrack | 60301003 | Film out of window | The film is not within the allowed window.
446 | HXX/FilmTrack | 60301010 | Film tracking sensor is dirty | Description: The film tracking sensor needs to be cleaned.
447 | HXX/FilmTrack | 60301010 | Film tracking sensor is dirty | Description: The film tracking sensor needs to be cleaned.
448 | HXX/FilmTrack | 60301013 | Circuit breaker film tracking | Description: The circuit breaker for the film tracking is switched off.
449 | HXX/FilmTrack | 60301013 | Circuit breaker film tracking | Description: The circuit breaker for the film tracking is switched off.
450 | HXX/Splicer | 60302000 | Add new roll of film | One film roll is empty.
451 | HXX/Splicer | 60302001 | Both film reels are empty | Both film reels are empty.
452 | HXX/SpliceInsp | 60307001 | Missing splice signal | There was a splice with a tape at inside of film which has to be detected with the splice supervision lightswitch. If there was no tape detected this fault occures
453 | HXX/NGNS | 60308000 | Validation fault | The module detected a value out of range.
454 | HXX/NGNS | 60308001 | No gap no seal detected over several cycles | No gap no seal has been detected continuously over several cycles.
455 | HXX/NGNS | 60308002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
456 | HXX/Printer | 60309000 | Message | The printer shows a message that does not lead to a machine stop (e.g. toner low).
457 | HXX/Printer | 60309001 | Not ready | The machine has been stopped due to an error of the printer.
458 | HXX/Printer | 60309002 | Circuit breaker | The printer circuit breaker is switched off.
459 | HXX/Printer | 60309003 | Filter Fault | The machine has been stopped due to an error of the printer filter.
460 | HXX/Printer | 60309004 | Filter Full | The Filter shows a message that the Filter is more than 75% full.
461 | HXX/Printer | 60309005 | Circuit breaker fume extractor | The fume extractor circuit breaker is switched off.
462 | HXX/SwiLev | 60317000 | Drive fault | The drive controller of this motor is reporting a fault condition.
463 | HXX/SwiLev | 60317003 | Validation fault | The module detected a value out of range.
464 | HXX/SwiLev | 60317011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
465 | HXX/SwiLev | 60317012 | Film is broken | The swingarm is at zero position.
466 | HXX/CutLengthMeas | 60318000 | Bad registration marks LS1 | A consecutive number of marks or flickers have been out of position. This could either mean that there are too many marks or that the sensor is flickering.
467 | HXX/CutLengthMeas | 60318001 | Bad registration marks LS2 | A consecutive number of marks or flickers have been out of position. This could either mean that there are too many marks or that the sensor is flickering.
468 | HPS | 60320001 | Splice process active | The splice process is active. The second roll is geared and both rolls are turning and synchronising. The splice process ends by cutting the film end and stopping the old roll. This is only an information.
469 | HPS | 60320002 | Emergency splice active | Emergency splice process is active. The button to do an emergency splice was activated. This process ends if the new roll is in place with its rape and the splicer arm is in splice position as well. This is only an information.
470 | HPS | 60320003 | New roll too small | The diameter of the new measured roll is too small. It's not worth to start running this roll.
471 | HPS | 60320004 | Check encoder wheel measuring arm | The encoder wheel of the measuring arm measured an invalid roll diameter.
472 | HPS | 60320005 | Mark on new roll not found | There was no registration mark found on the new roll.
473 | HPS | 60320006 | Tape on new roll not found | There was no tape found on the new roll.
474 | HPS | 60320007 | Wrong cut off length on new roll | The measured cut-off length is not compatible with the preset cut-off length on parameter values of the HMI. The mounted film roll is most probably the wrong one.
475 | HPS | 60320008 | Tape on cut position | The tape was detected on cut position. This leads to dirty knives at crosseal
476 | HPS | 60320010 | No new roll successfully prepared | There was no new roll loaded - or the loaded roll was bad.
477 | HPS | 60320011 | One roll empty | One film roll is empty.
478 | HPS | 60320013 | Simulation active | The simulation of the splice function is activated.
479 | HPS | 60320014 | Teach mode active | The teach mode is active. The machine won't start. With the jog button it is possible to move the measuring roll to teach the sensor to the registration mark or to the tape
480 | HPS | 60320015 | Check film | Check if the film is correctly threaded.
481 | HPS | 60320016 | Cut film manually needed | The knife is disabled. You need to cut the paper manually (after a desired adjusted lap length)
482 | HPS | 60320017 | Check splicer reg mark sensor | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
483 | HPS/Saf | 60321011 | Film roll access door open | There is an open door.
484 | HPS/Saf | 60321012 | Film roll access door open | There is an open door.
485 | HPS/Saf | 60321013 | Roll 1 mute switch fault | The mute switch to bypass the door is faulted.
486 | HPS/Saf | 60321014 | Roll 2 mute switch fault | The mute switch to bypass the door is faulted.
487 | HPS/Saf | 60321080 | Energize drives fault HPS | The energizing of the drives is faulted.
488 | HPS/Saf | 60321081 | Energize drives fault HPS Roll 1 | The energizing of the drives is faulted.
489 | HPS/Saf | 60321082 | Energize drives fault HPS Roll 2 | The energizing of the drives is faulted.
490 | HPS/Saf | 60321090 | Exhaust valve fault | The exhaust valve has a fault.
491 | HPS/Saf | 60321091 | Restarting exhaust valve | The exhaust valve is restarting.
492 | HPS/Saf | 60321092 | Energize exhaust valve fault | The energizing of the valve is faulted.
493 | HPS/Saf | 60321093 | Air pressure too low | The air pressure is below the allowed operating level.
494 | HPS/Saf | 60321094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
495 | HPS/Revolver | 60322000 | Drive fault | The drive controller of this motor is reporting a fault condition.
496 | HPS/Revolver | 60322001 | Position error | The controlled motor is out of the commanded position.
497 | HPS/Revolver | 60322002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
498 | HPS/Revolver | 60322003 | Validation fault | The module detected a value out of range.
499 | HPS/Revolver | 60322004 | Switched off | The motor has been switched off temporarily.
500 | HPS/Revolver | 60322007 | Brake manually released | The electrical brake of the cross seal motor is manually released.
501 | HPS/Revolver | 60322010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
502 | HPS/Revolver | 60322011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
503 | HPS/Roll1 | 60323000 | Drive fault | The drive controller of this motor is reporting a fault condition.
504 | HPS/Roll1 | 60323001 | Position error | The controlled motor is out of the commanded position.
505 | HPS/Roll1 | 60323002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
506 | HPS/Roll1 | 60323003 | Validation fault | The module detected a value out of range.
507 | HPS/Roll1 | 60323004 | Switched off | The motor has been switched off temporarily.
508 | HPS/Roll2 | 60324000 | Drive fault | The drive controller of this motor is reporting a fault condition.
509 | HPS/Roll2 | 60324001 | Position error | The controlled motor is out of the commanded position.
510 | HPS/Roll2 | 60324002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
511 | HPS/Roll2 | 60324003 | Validation fault | The module detected a value out of range.
512 | HPS/Roll2 | 60324004 | Switched off | The motor has been switched off temporarily.
513 | HPS/SwiLev | 60325000 | Drive fault | The drive controller of this motor is reporting a fault condition.
514 | HPS/SwiLev | 60325003 | Validation fault | The module detected a value out of range.
515 | HPS/SwiLev | 60325011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
516 | HPS/SwiLev | 60325012 | Film is broken | The swingarm is at zero position.
517 | HPS/Splicer | 60326000 | Drive fault | The drive controller of this motor is reporting a fault condition.
518 | HPS/Splicer | 60326001 | Position error | The controlled motor is out of the commanded position.
519 | HPS/Splicer | 60326002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
520 | HPS/Splicer | 60326003 | Validation fault | The module detected a value out of range.
521 | HPS/Splicer | 60326004 | Switched off | The motor has been switched off temporarily.
522 | HPS/Splicer | 60326007 | Motor brake manually released | The electrical brake of the cross seal motor is manually released.
523 | HPS/Splicer | 60326010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
524 | HPS/Splicer | 60326011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
525 | HPS/MeasArm | 60327000 | End switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
526 | HPS/MeasArm | 60327001 | Cylinder blocked | The end switch is still active, although the cyclinder was activated.
527 | HPS/EncMeasArm | 60328000 | Drive fault | The drive controller of this motor is reporting a fault condition.
528 | HPS/EncMeasArm | 60328003 | Validation fault | The module detected a value out of range.
529 | HPS/RollClamp | 60329000 | Clamp end switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
530 | HPS/RollClamp | 60329001 | Clamp cylinder blocked | The end switch is still active, although the cyclinder was activated.
531 | HPS/RollClamp | 60329002 | Stopper end switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
532 | HPS/RollClamp | 60329003 | Stopper cylinder blocked | The end switch is still active, although the cyclinder was activated.
533 | HPS/Knife | 60330000 | End switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
534 | HPS/Knife | 60330001 | Cylinder blocked | The end switch is still active, although the cyclinder was activated.
535 | HXX/SAF | 60335035 | Cover printer open | There is a guard open.
536 | HXX/SAF | 60335036 | Printer not in work position | Printer is not in work position
537 | HXX/SAF | 60335081 | Energize printer fault | The energizing of the printer is faulted.
538 | HXX/OutfRej | 60350000 | Validation fault | The module detected a value out of range.
539 | HXX/OutfRej | 60350001 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
540 | HXX/OutfRej | 60350002 | Option to reject all products is enabled | The option to reject all products is enabled.
541 | HXX/OutfRejEmpty | 60351000 | Validation fault | The module detected a value out of range.
542 | HXX/OutfRejVerif | 60354000 | Validation fault | The module detected a value out of range.
543 | HXX/OutfRejVerif | 60354001 | Bad product was not rejected | The supervision of the outfeed rejection has detected a product that should have been rejected.
544 | HXX/OutfRejVerif | 60354002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will stop because of this.
545 | HXX/DoubleInsp | 60355000 | Validation fault | The module detected a value out of range.
546 | HXX/DoubleInsp | 60355001 | Double package rejected over several cycles | Double packages were rejected continuously over several cycles.
547 | HXX/DoubleInsp | 60355002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will stop because of this.
548 | HXX/OutfBeltVac | 60359000 | Circuit breaker | The circuit breaker is switched off.
549 | HXX/OutfBeltVac | 60359001 | Waiting for vacuum | The vacuum pump is starting up.
550 | HXX/OutfBeltVac | 60359002 | Drive fault | The drive controller of this motor is reporting a fault condition.
551 | HXX/OutfBeltVac | 60359003 | Validation fault | The module detected a value out of range.
552 | KA/VAxCrdBrd | 60500003 | Validation fault | The module detected a value out of range.
553 | KA/VAxCrdBrd | 60500008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
554 | KA/VAxCrdBrd | 60500011 | One cardboard reel empty | One of the two cardboard reels is emtpy.
555 | KA/VAxCrdBrd | 60500012 | Both cardboard reels are empty | Both cardboard reels are emtpy.
556 | KA/VAxCrdBrd | 60500013 | Cardboard reel empty | The cardboard reel is emtpy.
557 | KA/VAxCrdBrd | 60500015 | Message sup splice aktive | Message suplier splice aktive
558 | KA/VAxCrdBrd | 60500950 | Not displayed on HMI!
559 | KA/AxKnife | 60503000 | Drive fault | The drive controller of this motor is reporting a fault condition.
560 | KA/AxKnife | 60503001 | Position error | The controlled motor is out of the commanded position.
561 | KA/AxKnife | 60503002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
562 | KA/AxKnife | 60503003 | Validation fault | The module detected a value out of range.
563 | KA/AxKnife | 60503004 | Switched off | The motor has been switched off temporarily.
564 | KA/AxKnife | 60503006 | Proximity switch not found | During hard home procedure the home position could not been detected.
565 | KA/AxKnife | 60503008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
566 | KA/AxKnife | 60503010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
567 | KA/AxKnife | 60503011 | The top belt is not in working position | The top belt is not in working position
568 | KA/AxTrpUp | 60504000 | Drive fault | The drive controller of this motor is reporting a fault condition.
569 | KA/AxTrpUp | 60504001 | Position error | The controlled motor is out of the commanded position.
570 | KA/AxTrpUp | 60504002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
571 | KA/AxTrpUp | 60504003 | Validation fault | The module detected a value out of range.
572 | KA/AxTrpUp | 60504004 | Switched off | The motor has been switched off temporarily.
573 | KA/AxTrpUp | 60504010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
574 | KA/AxTrpUp | 60504011 | Cardboard jammed | The cardboard in the transport is jammed.
575 | KA/AxTrpLw | 60505000 | Drive fault | The drive controller of this motor is reporting a fault condition.
576 | KA/AxTrpLw | 60505001 | Position error | The controlled motor is out of the commanded position.
577 | KA/AxTrpLw | 60505002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
578 | KA/AxTrpLw | 60505003 | Validation fault | The module detected a value out of range.
579 | KA/AxTrpLw | 60505004 | Switched off | The motor has been switched off temporarily.
580 | KA/AxTrpLw | 60505010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
581 | KA/AxTrpLw | 60505011 | Cardboard jammed | The cardboard in the transport is jammed.
582 | KA/AxFeedChain | 60506000 | Drive fault | The drive controller of this motor is reporting a fault condition.
583 | KA/AxFeedChain | 60506001 | Position error | The controlled motor is out of the commanded position.
584 | KA/AxFeedChain | 60506002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
585 | KA/AxFeedChain | 60506003 | Validation fault | The module detected a value out of range.
586 | KA/AxFeedChain | 60506004 | Switched off | The motor has been switched off temporarily.
587 | KA/AxFeedChain | 60506006 | Proximity switch not found | During hard home procedure the home position could not been detected.
588 | KA/AxFeedChain | 60506008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
589 | KA/AxFeedChain | 60506010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
590 | KA/AxFeedChain | 60506011 | Top belt not in working position | The top belt after the knife is not in working position.
591 | KA/AxTrpCutBltUp | 60507000 | Drive fault | The drive controller of this motor is reporting a fault condition.
592 | KA/AxTrpCutBltUp | 60507001 | Position error | The controlled motor is out of the commanded position.
593 | KA/AxTrpCutBltUp | 60507002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
594 | KA/AxTrpCutBltUp | 60507003 | Validation fault | The module detected a value out of range.
595 | KA/AxTrpCutBltUp | 60507004 | Switched off | The motor has been switched off temporarily.
596 | KA/AxTrpCutBltUp | 60507008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
597 | KA/AxTrpCutBltUp | 60507010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
598 | KA/AxTrpCutBltLw | 60508000 | Drive fault | The drive controller of this motor is reporting a fault condition.
599 | KA/AxTrpCutBltLw | 60508001 | Position error | The controlled motor is out of the commanded position.
600 | KA/AxTrpCutBltLw | 60508002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
601 | KA/AxTrpCutBltLw | 60508003 | Validation fault | The module detected a value out of range.
602 | KA/AxTrpCutBltLw | 60508004 | Switched off | The motor has been switched off temporarily.
603 | KA/AxTrpCutBltLw | 60508008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
604 | KA/AxTrpCutBltLw | 60508010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
605 | H1 | 61009000 | Service mode active | The unit and the corresponding controlled leg belts are in Service mode. No rows will be distributed to this leg.
606 | H1 | 61009001 | Clean mode active | The unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
607 | H1 | 61009002 | Setup mode active | The unit and the corresponding controlled leg belts are in Setup mode. No rows will be distributed to this leg.
608 | H1 | 61009003 | Fill mode active | The unit and the corresponding controlled leg belts are in fill mode. No rows will be distributed to this leg.
609 | H1 | 61009004 | Empty mode active | The unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
610 | H1 | 61009005 | Simulation mode active | The unit and the corresponding controlled leg belts are in simulation mode. No rows will be distributed to this leg.
611 | H1/Saf | 61021030 | Door machine outfeed open | There is a guard open.
612 | H1/Saf | 61021032 | Cover machine outfeed open | There is a guard open.
613 | H1/Saf | 61021033 | Cover folding box open | There is a guard open.
614 | H1/Saf | 61021034 | Door longitudinal sealing open | There is a guard open.
615 | H1/Saf | 61021035 | Cover printer open | There is a guard open.
616 | H1/Saf | 61021036 | Main cover open | There is a guard open.
617 | H1/Saf | 61021037 | Door After ejector Acceleration Belt open | There is a guard open.
618 | H1/Saf | 61021038 | Cover infeed chain open | There is a guard open.
619 | H1/Saf | 61021039 | Door Before ejector Acceleration Belt is open | There is a guard open.
620 | H1/Saf | 61021040 | Door metering belt open | There is a guard open.
621 | H1/Saf | 61021041 | Printer not in work position | Printer is not in work position
622 | H1/Saf | 61021043 | Door infeed chain mc side open | There is a guard open.
623 | H1/Saf | 61021044 | Door infeed chain middle open | There is a guard open.
624 | H1/Saf | 61021045 | Door infeed chain infeed side open | There is a guard open.
625 | H1/Saf | 61021046 | Cover infeed chain mc side open | There is a guard open.
626 | H1/Saf | 61021047 | Cover infeed chain middle open | There is a guard open.
627 | H1/Saf | 61021048 | Cover infeed chain infeed side open | There is a guard open.
628 | H1/Saf | 61021050 | Door control belt open | There is a guard open.
629 | H1/Saf | 61021051 | Door alignment belt open | There is a guard open.
630 | H1/Saf | 61021052 | Side alignment belt out of operating position | The alignment side belt is not in operating position.
631 | H1/Saf | 61021053 | Door turning belts open | There is a guard open.
632 | H1/Saf | 61021054 | Door after metal detector open | There is a guard open.
633 | H1/Saf | 61021055 | Door before metal detector open | There is a guard open.
634 | H1/Saf | 61021056 | Door alignment belt back open | There is a guard open.
635 | H1/Saf | 61021057 | Door after metal detector back open | There is a guard open.
636 | H1/Saf | 61021058 | Side guide rear side out of operating position | The side guide rear side is not in operating position.
637 | H1/Saf | 61021059 | Side guide front side out of operating position | The side guide front side is not in operating position.
638 | H1/Saf | 61021060 | Cover metering belt open | There is a guard open.
639 | H1/Saf | 61021061 | Cover control belt open | There is a guard open.
640 | H1/Saf | 61021062 | Door alignment belt mc side open | There is a guard open.
641 | H1/Saf | 61021063 | Door alignment belt middle open | There is a guard open.
642 | H1/Saf | 61021064 | Door alignment belt infeed side open | There is a guard open.
643 | H1/Saf | 61021065 | Door control belt mc side open | There is a guard open.
644 | H1/Saf | 61021066 | Door control belt middle open | There is a guard open.
645 | H1/Saf | 61021067 | Door control belt infeed side open | There is a guard open.
646 | H1/Saf | 61021068 | Door ejector Acceleration Belt open | There is a guard open.
647 | H1/Saf | 61021070 | Cover acceleration belt open | There is a guard open.
648 | H1/Saf | 61021074 | Door under curve chain open | There is a guard open.
649 | H1/Saf | 61021075 | Cover curve chain open | There is a guard open.
650 | H1/Saf | 61021080 | Energize drives fault HXX | The energizing of the drives is faulted.
651 | H1/Saf | 61021081 | Energize drives fault FXX | The energizing of the drives is faulted.
652 | H1/Saf | 61021082 | Energize drives fault Chain Switch | The energizing of the drives is faulted.
653 | H1/Saf | 61021085 | Energize drives fault Cab 1 | The energizing of the drives is faulted.
654 | H1/Saf | 61021086 | Energize drives fault Cab 2 | The energizing of the drives is faulted.
655 | H1/Saf | 61021087 | Energize drives fault Cab 3 | The energizing of the drives is faulted.
656 | H1/Saf | 61021090 | Exhaust valve fault | The exhaust valve has a fault.
657 | H1/Saf | 61021091 | Restarting exhaust valve | The exhaust valve is restarting.
658 | H1/Saf | 61021092 | Energize exhaust valve fault | The energizing of the valve is faulted.
659 | H1/Saf | 61021093 | Air pressure too low | The air pressure is below the allowed operating level.
660 | H1/Saf | 61021094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
661 | H1/Saf | 61021100 | Door FBM open | There is a guard open.
662 | H1/Saf | 61021101 | Cover FBM open | There is a guard open.
663 | H1/Saf | 61021102 | Door FDM open | There is a guard open.
664 | H1/Saf | 61021103 | Cover FDM open | There is a guard open.
665 | H1/Saf | 61021110 | Door feeding wheel front side open | There is a guard open.
666 | H1/Saf | 61021111 | Door feeding wheel rear side open | There is a guard open.
667 | H1/Saf | 61021112 | Door feeding wheel infeed open | There is a guard open.
668 | H1/Saf | 61021113 | Door feeding wheel outfeed open | There is a guard open.
669 | H1/Saf | 61021120 | Door grouping chain open | There is a guard open.
670 | H1/Saf | 61021121 | Cover grouping chain open | There is a guard open.
671 | H1/Saf | 61021130 | Door folding box open | There is a guard open.
672 | H1/Saf | 61021130 | Door cardboard feeder open | There is a guard open.
673 | H1/Saf | 61021131 | Cover cardboard feeder open | There is a guard open.
674 | H1/Saf | 61021132 | Door cardboard chain open | There is a guard open.
675 | H1/Saf | 61021142 | Transport side belt 2 out of operating position | The transport side belt is not in operating position.
676 | H1/Saf | 61021143 | Transport side belt 3 out of operating position | The transport side belt is not in operating position.
677 | H1/Saf | 61021144 | Transport side belt 4 out of operating position | The transport side belt is not in operating position.
678 | H1/UIface | 61030000 | Ethernet communication fault with upstream | An ethernet fault with the upstream is active.
679 | H1/UIface | 61030001 | Interface signals overridden | The downstream interface signals are overridden
680 | H1/UIface | 61030002 | Upstream not ready | The upstream equipment is not ready.
681 | H1/DIface | 61031000 | Ethernet communication fault with downstream | An ethernet fault with the downstream is active.
682 | H1/DIface | 61031001 | Interface signals overridden | The downstream interface signals are overridden
683 | H1/DIface | 61031002 | Downstream not ready | The downstream equipment is not ready.
684 | H1/DIface | 61031003 | Check weigher not running or faulted | HCM is not allowed to produce to TTM before check weigher is running
685 | HPS | 61210000 | New roll is preparing for splice | This is a ready stop until the splice is prepared. The position of the working film roll is just before the splice - it is not allowed to run the machine until the preparation of the splice is completed.
686 | H1/OfdDvrt | 61901000 | Diverter in diverted position | The diverter at the downstream is in the diverted position.
687 | H1/OfdDvrt | 61901001 | Remove products from outfeed belt | Remove products from outfeed belt
688 | H1/OfdDvrt | 61901002 | Retail not ready | The switch is in the position RETAIL, but the retail is not ready.
689 | H1/OfdDvrt | 61901003 | Bulk not ready | The switch is in the position BULK, but the bulk is not ready.
690 | H1/OfdDvrt | 61901004 | Validation fault | The module detected a value out of range.
PLC 1 Data
Data# | Processor Tag |  | Value | Concentrator Tag | Path IP | Description | Python Variable Name
1 | [HCM273]HXX_SM_Iface.State.b_run |  | 1 | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.37 | Machine Running
2 | [HCM273]HXX_SM_Iface.Mode.b_production &not [HCM273]HXX_SM_iface.State.b_Alarm &not [HCM273]Ctrliface.b_running |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[0].1 | 10.168.100.37 | Machine Ready (Stopped)
3 | [HCM273]HXX_SM_Iface.Mode.b_production &not [HCM273]HXX_SM_iface.State.b_Alarm & [HCM273]Ctrliface.b_running &not [HCM273]HXX_SM_Iface.State.b_run |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[0].2 | 10.168.100.37 | Machine Ready (Waiting)
4 | [HCM273]HXX_SM_iface.State.b_Alarm |  | 1 | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[0].10 | 10.168.100.37 | Alarm Present
5 | [HCM273]HMI_Cmd.BtnEnShift1.b_Active |  | 1 | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[0].11 | 10.168.100.37 | Shift 1 Enabled
6 | [HCM273]HMI_Cmd.BtnEnShift2.b_Active |  | 1 | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[0].12 | 10.168.100.37 | Shift 2 Enabled
7 | [HCM273]HMI_Cmd.BtnEnShift3.b_Active |  | 1 | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[0].13 | 10.168.100.37 | Shift 3 Enabled
8 | [HCM273]HXX_SvAccProdInsp_HMI.Counter.dn_ProdWaste |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[9] | 10.168.100.37 | Pieces Rejected at Lug Chain | hcm_273_pieces_rejected_at_lug_chain
9 | [HCM273HXX_GLB_Iface.dn_ProdPerPack |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.37 | Pieces per Package | hcm_273_pieces_per_pack
10 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_PacksIn |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[11] | 10.168.100.37 | Packages into Wrapper | hcm_273_packages_into_wrapper
11 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_PacksWaste |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.37 | Packages Rejected Waste | hcm_273_packages_rejected_waste
12 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_PacksOut |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[13] | 10.168.100.37 | Packages Out From Wrapper | hcm_273_packs_out_from_wrapper
13 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_Double Pack |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[14] | 10.168.100.37 | Double Packages Rejected | hcm_273_double_packages_rejected
14 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_TooShortProd |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[15] | 10.168.100.37 | Packages Rejected Too Short | hcm_273_packages_rejected_too_short
15 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_TooLongProd |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[16] | 10.168.100.37 | Packages Rejected Too Long | hcm_273_packages_rejected_too_long
16 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_EmptyPack |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[17] | 10.168.100.37 | Packages Rejected Empty | hcm_273_packages_rejected_empty
17 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_OutOfRegist |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.37 | Packages Rejected Out Of Registration | hcm_273_packages_rejected_out_of_registration
18 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_Splice |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.37 | Packages Rejected During Splice | hcm_273_packages_rejected_during_splice
19 | [HCM273]STA_Hmi.PresentShift.Performance_OfdRej.dn_SupSplice |  | Var | ComData_HCM_273_1_Alpha_To_Skynet.Status_Bits[20] | 10.168.100.37 | Packages Rejected Supplier Splice | hcm_273_packages_rejected_supplier_splice
20 | [HCM273]STA_Hmi.PresentShift.OEE.r_OEE |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Process_Values[10] |  | OEE | hcm_273_oee
21 | [HCM273]STA_Hmi.PresentShift.OEE.r_Availability |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Process_Values[11] |  | Availability | hcm_273_availability
22 | [HCM273]STA_Hmi.PresentShift.Performance_Mc.r_PacksPerMinute |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Process_Values[13] |  | Bars per Minute | hcm_273_bars_min_out
23 | [HCM273]HMI_Cmd.Dn_StartHoursShift1 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[0] | 10.168.100.37 | Start Time Hours Shift 1
24 | [HCM273]HMI_Cmd.Dn_StartMinutesShift1 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[1] | 10.168.100.37 | Start Time Minutes Shift 1
25 | [HCM273]HMI_Cmd.Dn_StartHoursShift2 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[2] | 10.168.100.37 | Start Time Hours Shift 2
26 | [HCM273]HMI_Cmd.Dn_StartMinutesShift2 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[3] | 10.168.100.37 | Start Time Minutes Shift 2
27 | [HCM273]HMI_Cmd.Dn_StartHoursShift3 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[4] | 10.168.100.37 | Start Time Hours Shift 3
28 | [HCM273]HMI_Cmd.Dn_StartMinutesShift3 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[5] | 10.168.100.37 | Start Time Minutes Shift 3
29 | [HCM273]HMI_Cmd.Dn_EndHoursShift1 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[6] | 10.168.100.37 | End Time Hours Shift 1
30 | [HCM273]HMI_Cmd.Dn_EndMinutesShift1 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[7] | 10.168.100.37 | End Time Minutes Shift 1
31 | [HCM273]HMI_Cmd.Dn_EndHoursShift2 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[8] | 10.168.100.37 | End Time Hours Shift 2
32 | [HCM273]HMI_Cmd.Dn_EndMinutesShift2 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[9] | 10.168.100.37 | End Time Minutes Shift 2
33 | [HCM273]HMI_Cmd.Dn_EndHoursShift3 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[10] | 10.168.100.37 | End Time Hours Shift 3
34 | [HCM273]HMI_Cmd.Dn_EndMinutesShift3 |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[11] | 10.168.100.37 | End Time Minutes Shift 3
32 | [HCM273]HMI_dn_Hour |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[12] | 10.168.100.37 | Current Hour In Processor
33 | [HCM273]HMI_dn_Minute |  | Var | ComData_HCM_273_Alpha_To_Skynet.Parameters[13] | 10.168.100.37 | Current Minute In Processor
34 | [HCM273]SM.Errors.DynText.List[0].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[0] | 10.168.100.37 | Dynamic Text Fault List 0
35 | [HCM273]SM.Errors.DynText.List[1].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[1] | 10.168.100.37 | Dynamic Text Fault List 1
36 | [HCM273]SM.Errors.DynText.List[2].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[2] | 10.168.100.37 | Dynamic Text Fault List 2
37 | [HCM273]SM.Errors.DynText.List[3].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[3] | 10.168.100.37 | Dynamic Text Fault List 3
38 | [HCM273]SM.Errors.DynText.List[4].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[4] | 10.168.100.37 | Dynamic Text Fault List 4
39 | [HCM273]SM.Errors.DynText.List[5].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[5] | 10.168.100.37 | Dynamic Text Fault List 5
40 | [HCM273]SM.Errors.DynText.List[6].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[6] | 10.168.100.37 | Dynamic Text Fault List 6
41 | [HCM273]SM.Errors.DynText.List[7].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[7] | 10.168.100.37 | Dynamic Text Fault List 7
42 | [HCM273]SM.Errors.DynText.List[8].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[8] | 10.168.100.37 | Dynamic Text Fault List 8
43 | [HCM273]SM.Errors.DynText.List[9].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[9] | 10.168.100.37 | Dynamic Text Fault List 9
44 | [HCM273]SM.Errors.FixText.List[0].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[30] | 10.168.100.37 | Fixed Text Fault List 0
45 | [HCM273]SM.Errors.FixText.List[1].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[31] | 10.168.100.37 | Fixed Text Fault List 1
46 | [HCM273]SM.Errors.FixText.List[2].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[32] | 10.168.100.37 | Fixed Text Fault List 2
47 | [HCM273]SM.Errors.FixText.List[3].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[33] | 10.168.100.37 | Fixed Text Fault List 3
48 | [HCM273]SM.Errors.FixText.List[4].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[34] | 10.168.100.37 | Fixed Text Fault List 4
49 | [HCM273]SM.Errors.FixText.List[5].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[35] | 10.168.100.37 | Fixed Text Fault List 5
50 | [HCM273]SM.Errors.FixText.List[6].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[36] | 10.168.100.37 | Fixed Text Fault List 6
51 | [HCM273]SM.Errors.FixText.List[7].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[37] | 10.168.100.37 | Fixed Text Fault List 7
52 | [HCM273]SM.Errors.FixText.List[8].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[38] | 10.168.100.37 | Fixed Text Fault List 8
53 | [HCM273]SM.Errors.FixText.List[9].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[39] | 10.168.100.37 | Fixed Text Fault List 9
54 | [HCM273]SM.Errors.FixText.List[10].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[40] | 10.168.100.37 | Fixed Text Fault List 10
55 | [HCM273]SM.Errors.FixText.List[11].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[41] | 10.168.100.37 | Fixed Text Fault List 11
56 | [HCM273]SM.Errors.FixText.List[12].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[42] | 10.168.100.37 | Fixed Text Fault List 12
57 | [HCM273]SM.Errors.FixText.List[13].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[43] | 10.168.100.37 | Fixed Text Fault List 13
58 | [HCM273]SM.Errors.FixText.List[14].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[44] | 10.168.100.37 | Fixed Text Fault List 14
59 | [HCM273]SM.Errors.FixText.List[15].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[45] | 10.168.100.37 | Fixed Text Fault List 15
60 | [HCM273]SM.Errors.FixText.List[16].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[46] | 10.168.100.37 | Fixed Text Fault List 16
61 | [HCM273]SM.Errors.FixText.List[17].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[47] | 10.168.100.37 | Fixed Text Fault List 17
62 | [HCM273]SM.Errors.FixText.List[18].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[48] | 10.168.100.37 | Fixed Text Fault List 18
63 | [HCM273]SM.Errors.FixText.List[19].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[49] | 10.168.100.37 | Fixed Text Fault List 19
64 | [HCM273]SM.Errors.FixText.List[20].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[50] | 10.168.100.37 | Fixed Text Fault List 20
65 | [HCM273]SM.Errors.FixText.List[21].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[51] | 10.168.100.37 | Fixed Text Fault List 21
66 | [HCM273]SM.Errors.FixText.List[22].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[52] | 10.168.100.37 | Fixed Text Fault List 22
67 | [HCM273]SM.Errors.FixText.List[23].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[53] | 10.168.100.37 | Fixed Text Fault List 23
68 | [HCM273]SM.Errors.FixText.List[24].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[54] | 10.168.100.37 | Fixed Text Fault List 24
69 | [HCM273]SM.Errors.FixText.List[25].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[55] | 10.168.100.37 | Fixed Text Fault List 25
70 | [HCM273]SM.Errors.FixText.List[26].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[56] | 10.168.100.37 | Fixed Text Fault List 26
71 | [HCM273]SM.Errors.FixText.List[27].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[57] | 10.168.100.37 | Fixed Text Fault List 27
72 | [HCM273]SM.Errors.FixText.List[28].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[58] | 10.168.100.37 | Fixed Text Fault List 28
73 | [HCM273]SM.Errors.FixText.List[29].dn_ID |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[59] | 10.168.100.37 | Fixed Text Fault List 29
74 | [HCM273]SM.Errors.DynText.dn_LastPos |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[60] | 10.168.100.37 | Position of Last stored position in Dyn List
75 | [HCM273]SM.Errors.FixText.dn_LastPos |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[61] | 10.168.100.37 | Position of Last stored position in Fix List
76 | [HCM273]SM.Errors.DynText.dn_EmptyPos |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[62] | 10.168.100.37 | Position of Next stored position in Dyn List
77 | [HCM273]SM.Errors.FixText.dn_EmptyPos |  | Var | ComData_HCM_273_Alpha_To_Skynet.Fault_data[63] | 10.168.100.37 | Position of Next stored position in Fix List
PLC 2 Data
1 | [HCM273]UIFace_DXX_OUT.b_ready |  | 1 | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.37:2 | FXX Infeed Runnning
2 | [HCM273]STA_Hmi.PresentShift.Performance_MetalRej.dn_ProdIn |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.37 | Pieces Received at Metal Detector | hcm_273_pieces_received_at_metal_detector
3 | [HCM273]STA_Hmi.PresentShift.Performance_MetalRej.dn_ProdWaste |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[11] | 10.168.100.37 | Rejected Count for Metal Detector
4 | [HCM273]STA_Hmi.PresentShift.Performance_MetalRej.dn_ProdOut |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.37 | Pieces Passed Metal Detector | hcm_273_pieces_passed_metal_detector
5 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdIn |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[13] | 10.168.100.37 | Pieces received at 3D Profile Station | hcm_273_pieces_received_at_3d_profile_station
6 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdTooLong |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[14] | 10.168.100.37 | Rejected Count for Too Long | hcm_273_rejected_count_for_too_long
7 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdTooShort |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[15] | 10.168.100.37 | Rejected Count for Too Short | hcm_273_rejected_count_for_too_short
8 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdTooHigh |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[16] | 10.168.100.37 | Rejected Count for Too High | hcm_273_rejected_count_for_too_high
9 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdToowide |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[17] | 10.168.100.37 | Rejected Count for Too Wide | hcm_273_rejected_count_for_too_wide
10 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_GapTooSmall |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.37 | Rejected Count for Gap Too Small | hcm_273_rejected_count_for_gap_too_small
11 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdWaste |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.37 | Total of rejected Pieces at 3D Profile | hcm_273_total_of_rejected_pieces_at_3d_profile
12 | [HCM273]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdOut |  | Var | ComData_HCM_273_2_Alpha_To_Skynet.Status_Bits[20] | 10.168.100.37 | Pieces Passed 3D Profile Station | hcm_273_pieces_passed_3d_profile_station

## Alpha HCM 274
HMI Fault Messages:
# | Component | Fault Value | Error Text | Description
1 | PLC1/SMCtr | 1001000 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
2 | PLC1/SMCtr | 1001001 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
3 | PLC1/SMCtr | 1001002 | Too small | This is a system failure: the shown registration list is too small.
4 | PLC1/SMCtr | 1001003 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
5 | PLC1/SMCtr | 1001004 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
6 | PLC1/SMCtr | 1001005 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
7 | PLC1/SMCtr | 1001006 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
8 | PLC1/SMCtr | 1001007 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
9 | PLC1/SMCtr | 1001008 | Controller Timeout | Global Statemachine fault.
10 | PLC1/SMCtr | 1001009 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
11 | PLC1/SMCtr | 1001010 | State machine init - | This is a system failure.
12 | PLC1/SMCtr | 1001011 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
13 | HMI | 1002000 | Product setup download active | There was a request for a format download job, but the download is not finished yet.
14 | PLC1/CPU | 1003000 | Battery low | The voltage of the internal battery of the PLC is low.
15 | PLC1/CPU | 1003003 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout.
16 | GMS | 1004000 | Power supply 24 V DC | The 24 V DC power supply is not ok.
17 | GMS | 1004001 | Circuit breaker solenoids power | The circuit breaker for the solenoids power is switched off. This circuit is used basically for solenoids opening and closing longitudinal sealing rolls and splicer.
18 | GMS | 1004002 | Air pressure too low | The air pressure is below the allowed operating level.
19 | GMS | 1004003 | Circuit breaker CAB2 power | The circuit breaker is turned off.
20 | GMS | 1004004 | Circuit breaker CAB2 control power | The circuit breaker is turned off.
21 | GMS | 1004005 | Circuit breaker transformer sealing | The circuit breaker before the transformer for the sealing equipment is switched off.
22 | GMS | 1004006 | Circuit breaker CAB1 power | The circuit breaker is turned off.
23 | GMS | 1004010 | Aircondition unit CAB 1 message | The aircondition unit has an active message.
24 | GMS | 1004011 | Circuit breaker aircondition unit CAB 1 | The residual current circuit breaker for the aircondition unit is turned off.
25 | GMS | 1004012 | Aircondition unit CAB 2 message | The aircondition unit has an active message.
26 | GMS | 1004013 | Circuit breaker aircondition unit CAB 2 | The residual current circuit breaker for the aircondition unit is turned off.
27 | GMS | 1004020 | Circuit breaker Kinetix rack 1 | The circuit breaker is switched off.
28 | GMS | 1004021 | Circuit breaker control power Kinetix rack 1 | The circuit breaker is switched off.
29 | GMS | 1004022 | Circuit breaker Kinetix rack 2 | The circuit breaker is switched off.
30 | GMS | 1004023 | Circuit breaker control power Kinetix rack 2 | The circuit breaker is switched off.
31 | GMS | 1004024 | Circuit breaker Kinetix rack 3 | The circuit breaker is switched off.
32 | GMS | 1004025 | Circuit breaker control power Kinetix rack 3 | The circuit breaker is switched off.
33 | GMS | 1004026 | Circuit breaker Kinetix rack 4 | The circuit breaker is switched off.
34 | GMS | 1004027 | Circuit breaker control power Kinetix rack 4 | The circuit breaker is switched off.
35 | GMS | 1004028 | Circuit breaker Kinetix rack 5 | The circuit breaker is switched off.
36 | GMS | 1004029 | Circuit breaker control power Kinetix rack 5 | The circuit breaker is switched off.
37 | GMS | 1004040 | Circuit breaker power supply ultra sonic generator | The circuit breaker is switched off.
38 | PLC1/IO | 1005001 | Electronic fuse triggered on 2A digital output card | The electronic protection circuit of one the of digital output cards for 2A high power outputs of the PLC has been activated due to a short circuit.
39 | PLC1/IO | 1005002 | Missing remote I/O rack 00 | One of the Remote I/O modules is missing.
40 | PLC1/IO | 1005003 | Missing remote I/O rack 01 | One of the Remote I/O modules is missing.
41 | PLC1/IO | 1005004 | Missing remote I/O rack 02 | One of the Remote I/O modules is missing.
42 | PLC1/IO | 1005005 | Missing remote I/O rack 03 | One of the Remote I/O modules is missing.
43 | SAF1 | 1021006 | LOTO switch main cabinet turned off | The Lock Out Tag Out (LOTO) switch at main cabinet is turned off.
44 | SAF1 | 1021011 | Emergency stop machine | The emergency stop button is pressed or has already been disengaged.
45 | SAF1 | 1021013 | Emergency stop cardboard feeder | The emergency stop button is pressed or has already been disengaged.
46 | SAF1 | 1021015 | Emergency stop control belt | The emergency stop button is pressed or has already been disengaged.
47 | SAF1 | 1021016 | Emergency stop alignment belt | The emergency stop button is pressed or has already been disengaged.
48 | SAF1 | 1021017 | Emergency stop turning belts | The emergency stop button is pressed or has already been disengaged.
49 | SAF1 | 1021019 | Emergency stop distribution unit | The emergency stop button is pressed or has already been disengaged.
50 | SAF1 | 1021021 | Emergency stop infeed transport belts | The emergency stop button is pressed or has already been disengaged.
51 | SAF1 | 1021070 | Emergency stop feeding wheel front side | The emergency stop button is pressed or has already been disengaged.
52 | SAF1 | 1021071 | Emergency stop feeding wheel rear side | The emergency stop button is pressed or has already been disengaged.
53 | SAF1 | 1021072 | Emergency stop feeding wheel infeed | The emergency stop button is pressed or has already been disengaged.
54 | SAF1 | 1021073 | Emergency stop feeding wheel outfeed | The emergency stop button is pressed or has already been disengaged.
55 | SAF1 | 1021079 | Emergency stop customer | The emergency stop button from an other machine is pressed.
56 | SAF1 | 1021080 | Energize drives vacuum pump outfeed belt fault | The energizing of the drives is faulted.
57 | SAF1 | 1021081 | Energize vacuum pump metering belt fault | The energizing of the vacuum pump is faulted.
58 | SAF1 | 1021082 | Energize empty pack suction fault | The energizing of the vacuum pump is faulted.
59 | SAF1 | 1021083 | Energize vacuum pump longitudinal fault | The energizing of the vacuum pump is faulted.
60 | SAF1 | 1021084 | Energize drives longitudinal vacuum pump fault | The energizing of the drives is faulted.
61 | SAF1 | 1021085 | Energize drives empty pack suction fault | The energizing of the drives is faulted.
62 | SAF1 | 1021090 | Exhaust valve fault | The exhaust valve has a fault.
63 | SAF1 | 1021091 | Restarting exhaust valve | The exhaust valve is restarting.
64 | SAF1 | 1021092 | Energize exhaust valve fault | The energizing of the valve is faulted.
65 | SAF1 | 1021093 | Air pressure too low | The air pressure is below the allowed operating level.
66 | SAF1 | 1021094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
67 | PLC1/STA | 1051001 | No SD card | The SD card in the controller is missing
68 | PLC1/STA | 1051002 | SD card write error | The Prozessor has a problem to write the datas to the SD card
69 | PLC1/STA | 1051003 | SD card read error | The Prozessor has a problem to read the datas from the SD card
70 | PLC2/SMCtr | 2001000 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
71 | PLC2/SMCtr | 2001001 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
72 | PLC2/SMCtr | 2001002 | Too small | This is a system failure: the shown registration list is too small.
73 | PLC2/SMCtr | 2001003 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
74 | PLC2/SMCtr | 2001004 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
75 | PLC2/SMCtr | 2001005 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
76 | PLC2/SMCtr | 2001006 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
77 | PLC2/SMCtr | 2001007 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
78 | PLC2/SMCtr | 2001008 | Controller Timeout | Global Statemachine fault.
79 | PLC2/SMCtr | 2001009 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
80 | PLC2/SMCtr | 2001010 | State machine init - | This is a system failure.
81 | PLC2/SMCtr | 2001011 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
82 | PLC2/CPU | 2003000 | Battery low | The voltage of the internal battery of the PLC is low.
83 | PLC2/CPU | 2003003 | Communication fault to HMI | The handshake between this processor and the HMI is not working => timeout.
84 | PLC2/CPU | 2003010 | Please open the safety circuit | For the update of a conversion constante of a consumed axis is an open safety circuit required. Pleace open a guard or press the emergency stop.
85 | PLC2/IO | 2005001 | Electronic fuse triggered on 2A digital output card | The electronic protection circuit of one the of digital output cards for 2A high power outputs of the PLC has been activated due to a short circuit.
86 | PLC2/IO | 2005002 | Missing remote I/O rack 00 | One of the Remote I/O modules is missing.
87 | PLC2/IO | 2005003 | Missing remote I/O rack 01 | One of the Remote I/O modules is missing.
88 | PLC2/IO | 2005004 | Missing remote I/O rack 02 | One of the Remote I/O modules is missing.
89 | PLC2/IO | 2005005 | Missing remote I/O rack 03 | One of the Remote I/O modules is missing.
90 | PLC2/STA | 2051001 | No SD card | The SD card in the controller is missing
91 | PLC2/STA | 2051002 | SD card write error | The Prozessor has a problem to write the datas to the SD card
92 | PLC2/STA | 2051003 | SD card read error | The Prozessor has a problem to read the datas from the SD card
93 | FXX1/SM | 51010000 | State timeout | This is a system failure of this unit. There was a timeout in a state that needed to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
94 | FXX1/SM | 51010002 | Calculation active | There was a request for a calculation job, but the calculation is not finished yet.
95 | FXX1/SM | 51010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
96 | FXX1 | 51012000 | A feeding part is not homed | The home procedure has not been carried out yet.
97 | FXX1 | 51012001 | Feeder is homing | The feeding system is homing or synchronising
98 | FXX1/Speed Nose | 51060001 | Validation fault | Validation fault of the speed module "nose".
99 | FXX1/Speed | 51060002 | Sensor plus correction not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
100 | FXX1/Speed | 51060003 | Sensor minus correction not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
101 | FXX1/Speed | 51060004 | Overflow at infeed | The proportional photoeye did not detect any gap for a few products.
102 | FXX1/Speed | 51060005 | Check proportional photoeye | The photoeye detecting the incoming product has seen too many too small products.
103 | FXX1/Speed | 51060006 | Sensor proportional photoeye not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
104 | FXX1/Speed | 51060010 | Production stopped - infeed belts stopped | The belts stopped because there was no product coming in for a certain time.
105 | FXX1/TranspBelt1 | 51201000 | Drive fault | The drive controller of this motor is reporting a fault condition.
106 | FXX1/TranspBelt1 | 51201001 | Position error | The controlled motor is out of the commanded position.
107 | FXX1/TranspBelt1 | 51201002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
108 | FXX1/TranspBelt1 | 51201003 | Validation fault | The module detected a value out of range.
109 | FXX1/TranspBelt1 | 51201004 | Switched off | The motor has been switched off temporarily.
110 | FXX1/TranspBelt2 | 51202000 | Drive fault | The drive controller of this motor is reporting a fault condition.
111 | FXX1/TranspBelt2 | 51202001 | Position error | The controlled motor is out of the commanded position.
112 | FXX1/TranspBelt2 | 51202002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
113 | FXX1/TranspBelt2 | 51202003 | Validation fault | The module detected a value out of range.
114 | FXX1/TranspBelt2 | 51202004 | Switched off | The motor has been switched off temporarily.
115 | FXX1/TranspBelt3 | 51203000 | Drive fault | The drive controller of this motor is reporting a fault condition.
116 | FXX1/TranspBelt3 | 51203001 | Position error | The controlled motor is out of the commanded position.
117 | FXX1/TranspBelt3 | 51203002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
118 | FXX1/TranspBelt3 | 51203003 | Validation fault | The module detected a value out of range.
119 | FXX1/TranspBelt3 | 51203004 | Switched off | The motor has been switched off temporarily.
120 | FXX1/TurnBeltFront | 51221000 | Drive fault | The drive controller of this motor is reporting a fault condition.
121 | FXX1/TurnBeltFront | 51221001 | Position error | The controlled motor is out of the commanded position.
122 | FXX1/TurnBeltFront | 51221002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
123 | FXX1/TurnBeltFront | 51221003 | Validation fault | The module detected a value out of range.
124 | FXX1/TurnBeltFront | 51221004 | Switched off | The motor has been switched off temporarily.
125 | FXX1/TurnBeltRear | 51222000 | Drive fault | The drive controller of this motor is reporting a fault condition.
126 | FXX1/TurnBeltRear | 51222001 | Position error | The controlled motor is out of the commanded position.
127 | FXX1/TurnBeltRear | 51222002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
128 | FXX1/TurnBeltRear | 51222003 | Validation fault | The module detected a value out of range.
129 | FXX1/TurnBeltRear | 51222004 | Switched off | The motor has been switched off temporarily.
130 | FXX1/TurnBeltAcc | 51223000 | Drive fault | The drive controller of this motor is reporting a fault condition.
131 | FXX1/TurnBeltAcc | 51223001 | Position error | The controlled motor is out of the commanded position.
132 | FXX1/TurnBeltAcc | 51223002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
133 | FXX1/TurnBeltAcc | 51223003 | Validation fault | The module detected a value out of range.
134 | FXX1/TurnBeltAcc | 51223004 | Switched off | The motor has been switched off temporarily.
135 | FXX1/AlignBelt | 51224000 | Drive fault | The drive controller of this motor is reporting a fault condition.
136 | FXX1/AlignBelt | 51224001 | Position error | The controlled motor is out of the commanded position.
137 | FXX1/AlignBelt | 51224002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
138 | FXX1/AlignBelt | 51224003 | Validation fault | The module detected a value out of range.
139 | FXX1/AlignBelt | 51224004 | Switched off | The motor has been switched off temporarily.
140 | FXX1/AlignSideBelt | 51225000 | Drive fault | The drive controller of this motor is reporting a fault condition.
141 | FXX1/AlignSideBelt | 51225001 | Position error | The controlled motor is out of the commanded position.
142 | FXX1/AlignSideBelt | 51225002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
143 | FXX1/AlignSideBelt | 51225003 | Validation fault | The module detected a value out of range.
144 | FXX1/AlignSideBelt | 51225004 | Switched off | The motor has been switched off temporarily.
145 | FXX1/ControlBelt | 51226000 | Drive fault | The drive controller of this motor is reporting a fault condition.
146 | FXX1/ControlBelt | 51226001 | Position error | The controlled motor is out of the commanded position.
147 | FXX1/ControlBelt | 51226002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
148 | FXX1/ControlBelt | 51226003 | Validation fault | The module detected a value out of range.
149 | FXX1/ControlBelt | 51226004 | Switched off | The motor has been switched off temporarily.
150 | FXX1/ControlBelt2 | 51227000 | Drive fault | The drive controller of this motor is reporting a fault condition.
151 | FXX1/ControlBelt2 | 51227001 | Position error | The controlled motor is out of the commanded position.
152 | FXX1/ControlBelt2 | 51227002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
153 | FXX1/ControlBelt2 | 51227003 | Validation fault | The module detected a value out of range.
154 | FXX1/ControlBelt2 | 51227004 | Switched off | The motor has been switched off temporarily.
155 | FXX1/ControlBelt2 | 51227011 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
156 | FXX1/ControlBelt3 | 51228000 | Drive fault | The drive controller of this motor is reporting a fault condition.
157 | FXX1/ControlBelt3 | 51228001 | Position error | The controlled motor is out of the commanded position.
158 | FXX1/ControlBelt3 | 51228002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
159 | FXX1/ControlBelt3 | 51228003 | Validation fault | The module detected a value out of range.
160 | FXX1/ControlBelt3 | 51228004 | Switched off | The motor has been switched off temporarily.
161 | FXX1/ControlBelt3 | 51228011 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
162 | FBP/Nose | 51230000 | Drive fault | The drive controller of this motor is reporting a fault condition.
163 | FBP/Nose | 51230001 | Position error | The controlled motor is out of the commanded position.
164 | FBP/Nose | 51230002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
165 | FBP/Nose | 51230003 | Validation fault | The module detected a value out of range.
166 | FBP/Nose | 51230004 | Switched off | The motor has been switched off temporarily.
167 | FBP/Nose | 51230006 | Proximity switch not found | During hard home procedure the home position could not been detected.
168 | FBP/Nose | 51230008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
169 | FBP/Nose | 51230011 | Negative overtravel | The axis has exceeded the software limit position in negative direction.
170 | FBP/Nose | 51230012 | Positive overtravel | The axis has exceeded the software limit position in positive direction.
171 | FXX1/Jam | 51240000 | Jam at infeed | Product jam at the infeed side of the machine.
172 | FXX1/Jam | 51240001 | Sensor jam at infeed not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
173 | FXX1/MetalDet | 51241000 | Circuit breaker | The circuit breaker for the metal detector is switched off.
174 | FXX1/MetalDet | 51241001 | Not ready | The metal detector is not ready.
175 | FXX1/MetalDet | 51241002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
176 | FXX1/MetalDet | 51241003 | Sensor back not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
177 | FXX1/MetalDet | 51241004 | Sensor verification not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
178 | FXX1/MetalDet | 51241005 | Product not rejected | Products were not rejected
179 | FXX1/MetalDet | 51241006 | Sensor verification back not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
180 | FXX1/MetalDet | 51241007 | Product not rejected back | Products were not rejected
181 | FXX1/3D Check | 51244001 | Sensor length detection not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
182 | FXX1/3D Check | 51244002 | Validation fault | The module detected a value out of range.
183 | HXX/SM | 60010000 | State timeout | This is a system failure of this unit. There was a timeout in a state that needed to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
184 | HXX/SM | 60010002 | Calculation active | There was a request for a calculation job, but the calculation is not finished yet.
185 | HXX/SM | 60010004 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
186 | HXX | 60012000 | Remove all products from the infeed | Position of the corresponding motor is no more valid.
187 | HXX | 60012001 | Remove all products between machine chain and film | Position of the corresponding motor is no more valid.
188 | HXX | 60012002 | Remove all products from the longitudinal sealing | Position of the corresponding motor is no more valid.
189 | HXX | 60012003 | Remove all products from the cross seal | Position of the corresponding motor is no more valid.
190 | HXX | 60012004 | Remove all products from the machine outfeed belt | Position of the corresponding motor is no more valid.
191 | HXX | 60012005 | Machine is not homed | The home procedure has not been carried out yet.
192 | HXX | 60012006 | Machine is homing | After a size or parameter change the axis will re-home to proximity switches.
193 | HXX | 60012007 | Machine is synchronizing | After an emergency stop or after moving one of the axes manually the axis will move back to the desired position.
194 | HXX | 60012008 | Remove cardboards from the cardboard chain | Remove cardboards from the cardboard chain
195 | HXX | 60050000 | Product dimensions validation fault | The module detected a value out of range.
196 | HXX | 60050002 | Finished emptying | The emptying of the machine is finsihed.
197 | HXX | 60101000 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
198 | HXX/FXXIface | 60105000 | No product at infeed | The machine has stopped because there is no product being fed to it.
199 | HXX/Heater | 60110001 | Circuit breaker | The heater circuit breaker is switched off.
200 | HXX/Heater | 60110002 | Heaters are in warm-up procedure | The heaters are in warm-up procedure.
201 | HXX/Heater | 60110003 | Caution! Heaters are still hot | The heaters have not cooled down yet.
202 | HXX/Heater | 60110004 | Heaters are in warm-up procedure | The heaters are in warm-up procedure.
203 | HXX/Heat Lng2 rear | 60111000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
204 | HXX/Heat Lng2 rear | 60111001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
205 | HXX/Heat Lng2 rear | 60111002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
206 | HXX/Heat Lng2 rear | 60111003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
207 | HXX/Heat Lng2 rear | 60111004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
208 | HXX/Heat Lng2 rear | 60111005 | Heating time too long | This heater needs too long to warm up.
209 | HXX/Heat Lng2 rear | 60111006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
210 | HXX/Heat Lng2 rear | 60111007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
211 | HXX/Heat Lng2 rear | 60111008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
212 | HXX/Heat Lng2 rear | 60111009 | Heating time too long | This heater needs too long to warm up.
213 | HXX/Heat Lng2 front | 60112000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
214 | HXX/Heat Lng2 front | 60112001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
215 | HXX/Heat Lng2 front | 60112002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
216 | HXX/Heat Lng2 front | 60112003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
217 | HXX/Heat Lng2 front | 60112004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
218 | HXX/Heat Lng2 front | 60112005 | Heating time too long | This heater needs too long to warm up.
219 | HXX/Heat Lng2 front | 60112006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
220 | HXX/Heat Lng2 front | 60112007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
221 | HXX/Heat Lng2 front | 60112008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
222 | HXX/Heat Lng2 front | 60112009 | Heating time too long | This heater needs too long to warm up.
223 | HXX/Heat Lng3 rear | 60113000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
224 | HXX/Heat Lng3 rear | 60113001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
225 | HXX/Heat Lng3 rear | 60113002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
226 | HXX/Heat Lng3 rear | 60113003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
227 | HXX/Heat Lng3 rear | 60113004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
228 | HXX/Heat Lng3 rear | 60113005 | Heating time too long | This heater needs too long to warm up.
229 | HXX/Heat Lng3 rear | 60113006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
230 | HXX/Heat Lng3 rear | 60113007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
231 | HXX/Heat Lng3 rear | 60113008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
232 | HXX/Heat Lng3 rear | 60113009 | Heating time too long | This heater needs too long to warm up.
233 | HXX/Heat Lng3 front | 60114000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
234 | HXX/Heat Lng3 front | 60114001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
235 | HXX/Heat Lng3 front | 60114002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
236 | HXX/Heat Lng3 front | 60114003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
237 | HXX/Heat Lng3 front | 60114004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
238 | HXX/Heat Lng3 front | 60114005 | Heating time too long | This heater needs too long to warm up.
239 | HXX/Heat Lng3 front | 60114006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
240 | HXX/Heat Lng3 front | 60114007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
241 | HXX/Heat Lng3 front | 60114008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
242 | HXX/Heat Lng3 front | 60114009 | Heating time too long | This heater needs too long to warm up.
243 | HXX/Heat Crs up1 | 60115000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
244 | HXX/Heat Crs up1 | 60115001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
245 | HXX/Heat Crs up1 | 60115002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
246 | HXX/Heat Crs up1 | 60115003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
247 | HXX/Heat Crs up1 | 60115004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
248 | HXX/Heat Crs up1 | 60115005 | Heating time too long | This heater needs too long to warm up.
249 | HXX/Heat Crs up1 | 60115006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
250 | HXX/Heat Crs up1 | 60115007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
251 | HXX/Heat Crs up1 | 60115008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
252 | HXX/Heat Crs up1 | 60115009 | Heating time too long | This heater needs too long to warm up.
253 | HXX/Heat Crs up2 | 60116000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
254 | HXX/Heat Crs up2 | 60116001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
255 | HXX/Heat Crs up2 | 60116002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
256 | HXX/Heat Crs up2 | 60116003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
257 | HXX/Heat Crs up2 | 60116004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
258 | HXX/Heat Crs up2 | 60116005 | Heating time too long | This heater needs too long to warm up.
259 | HXX/Heat Crs up2 | 60116006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
260 | HXX/Heat Crs up2 | 60116007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
261 | HXX/Heat Crs up2 | 60116008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
262 | HXX/Heat Crs up2 | 60116009 | Heating time too long | This heater needs too long to warm up.
263 | HXX/Heat Crs low1 | 60118000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
264 | HXX/Heat Crs low1 | 60118001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
265 | HXX/Heat Crs low1 | 60118002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
266 | HXX/Heat Crs low1 | 60118003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
267 | HXX/Heat Crs low1 | 60118004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
268 | HXX/Heat Crs low1 | 60118005 | Heating time too long | This heater needs too long to warm up.
269 | HXX/Heat Crs low1 | 60118006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
270 | HXX/Heat Crs low1 | 60118007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
271 | HXX/Heat Crs low1 | 60118008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
272 | HXX/Heat Crs low1 | 60118009 | Heating time too long | This heater needs too long to warm up.
273 | HXX/Heat Crs low2 | 60119000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
274 | HXX/Heat Crs low2 | 60119001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
275 | HXX/Heat Crs low2 | 60119002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
276 | HXX/Heat Crs low2 | 60119003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
277 | HXX/Heat Crs low2 | 60119004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
278 | HXX/Heat Crs low2 | 60119005 | Heating time too long | This heater needs too long to warm up.
279 | HXX/Heat Crs low2 | 60119006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
280 | HXX/Heat Crs low2 | 60119007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
281 | HXX/Heat Crs low2 | 60119008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
282 | HXX/Heat Crs low2 | 60119009 | Heating time too long | This heater needs too long to warm up.
283 | HXX/PreHeat rear | 60121000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
284 | HXX/PreHeat rear | 60121001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
285 | HXX/PreHeat rear | 60121002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
286 | HXX/PreHeat rear | 60121003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
287 | HXX/PreHeat rear | 60121004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
288 | HXX/PreHeat rear | 60121005 | Heating time too long | This heater needs too long to warm up.
289 | HXX/PreHeat rear | 60121006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
290 | HXX/PreHeat rear | 60121007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
291 | HXX/PreHeat rear | 60121008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
292 | HXX/PreHeat rear | 60121009 | Heating time too long | This heater needs too long to warm up.
293 | HXX/PreHeat front | 60122000 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
294 | HXX/PreHeat front | 60122001 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
295 | HXX/PreHeat front | 60122002 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
296 | HXX/PreHeat front | 60122003 | Maximum temperature reached | The temperature of this heater has reached its highest possible temperature. The main heater contactor has been switched off.
297 | HXX/PreHeat front | 60122004 | Temperature probe | The temperature probe for this heater does not provide any signal. The heater has been turned off.
298 | HXX/PreHeat front | 60122005 | Heating time too long | This heater needs too long to warm up.
299 | HXX/PreHeat front | 60122006 | Temperature too low | The temperature of this heater is lower than its low setpoint limit.
300 | HXX/PreHeat front | 60122007 | Temperature too high | The temperature of this heater is higher than its high setpoint limit. The heater has been turned off.
301 | HXX/PreHeat front | 60122008 | Solid state relay too long active | The output for the solid state relay of this heater has been activated too long. The heater has been turned off for safety reasons.
302 | HXX/PreHeat front | 60122009 | Heating time too long | This heater needs too long to warm up.
303 | HXX/MetBeltVac | 60140000 | Circuit breaker | The circuit breaker is switched off.
304 | HXX/MetBeltVac | 60140001 | Waiting for vacuum | The vacuum pump is starting up.
305 | HXX/OutfVacEmpty | 60141000 | Circuit breaker | The circuit breaker is switched off.
306 | HXX/OutfVacEmpty | 60141001 | Waiting for vacuum | The vacuum pump is starting up.
307 | HXX/OutfVacEmpty | 60141002 | Drive fault | The drive controller of this motor is reporting a fault condition.
308 | HXX/OutfVacEmpty | 60141003 | Validation fault | The module detected a value out of range.
309 | HXX/OutfVacEmpty | 60141005 | Empty wrap vacuum isolater disconneted | The motor has been disconnected.
310 | HXX/SensorTeach | 60150000 | Sensor teaching is active | The sensor teaching ist active.
311 | HXX/VAxMaster | 60200008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
312 | HXX/VAxMaster | 60200010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
313 | HXX/VAxMaster | 60200012 | External speed too high | The speed of the external master axis is higher than maximum speed.
314 | HXX/NPNP | 60201008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
315 | HXX/NPNP | 60201010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
316 | HXX/Film | 60202008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
317 | HXX/Film | 60202010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
318 | HXX/NGNS | 60203008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
319 | HXX/NGNS | 60203010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
320 | HXX/VAxOutfBelt | 60204008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
321 | HXX/VAxOutfBelt | 60204010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
322 | HXX/OutfBelt | 60210001 | Position error | The controlled motor is out of the commanded position.
323 | HXX/OutfBelt | 60210002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
324 | HXX/OutfBelt | 60210003 | Validation fault | The module detected a value out of range.
325 | HXX/OutfBelt | 60210004 | Switched off | The motor has been switched off temporarily.
326 | HXX/OutfBelt | 60210008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
327 | HXX/OutfBelt | 60210010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
328 | HXX/Crs | 60211000 | Drive fault | The drive controller of this motor is reporting a fault condition.
329 | HXX/Crs | 60211001 | Position error | The controlled motor is out of the commanded position.
330 | HXX/Crs | 60211002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
331 | HXX/Crs | 60211003 | Validation fault | The module detected a value out of range.
332 | HXX/Crs | 60211004 | Switched off | The motor has been switched off temporarily.
333 | HXX/Crs | 60211006 | Proximity switch not found | During hard home procedure the home position could not been detected.
334 | HXX/Crs | 60211007 | Motor brake manually released | The electrical brake of the cross seal motor is manually released.
335 | HXX/Crs | 60211008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
336 | HXX/Crs | 60211010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
337 | HXX/Lng1 | 60212000 | Drive fault | The drive controller of this motor is reporting a fault condition.
338 | HXX/Lng1 | 60212001 | Position error | The controlled motor is out of the commanded position.
339 | HXX/Lng1 | 60212002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
340 | HXX/Lng1 | 60212003 | Validation fault | The module detected a value out of range.
341 | HXX/Lng1 | 60212004 | Switched off | The motor has been switched off temporarily.
342 | HXX/Lng1 | 60212005 | Film home selected | A film home has been selected or the film is out of synchronization.
343 | HXX/Lng1 | 60212008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
344 | HXX/Lng1 | 60212010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
345 | HXX/Lng1 | 60212011 | Bad registration marks detected | A consecutive number of marks or flickers have been out of position. This could either mean that there are too many marks or that the sensor is flickering.
346 | HXX/Lng1 | 60212012 | Registration mark not detected | The registration sensor did not see any registration mark for several cycles.
347 | HXX/Lng1 | 60212013 | Film registration error | The machine is unable to correct the registration to the specified tolerance.
348 | HXX/FilmFeeder | 60213000 | Drive fault | The drive controller of this motor is reporting a fault condition.
349 | HXX/FilmFeeder | 60213001 | Position error | The controlled motor is out of the commanded position.
350 | HXX/FilmFeeder | 60213002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
351 | HXX/FilmFeeder | 60213003 | Validation fault | The module detected a value out of range.
352 | HXX/FilmFeeder | 60213004 | Switched off | The motor has been switched off temporarily.
353 | HXX/FilmFeeder | 60213008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
354 | HXX/FilmFeeder | 60213010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
355 | HXX/InfChain | 60214000 | Drive fault | The drive controller of this motor is reporting a fault condition.
356 | HXX/InfChain | 60214001 | Position error | The controlled motor is out of the commanded position.
357 | HXX/InfChain | 60214002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
358 | HXX/InfChain | 60214003 | Validation fault | The module detected a value out of range.
359 | HXX/InfChain | 60214004 | Switched off | The motor has been switched off temporarily.
360 | HXX/InfChain | 60214006 | Proximity switch not found | During hard home procedure the home position could not been detected.
361 | HXX/InfChain | 60214008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
362 | HXX/InfChain | 60214010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
363 | HXX/InfChain | 60214011 | Flight check fault | During the "chain flight check" a chain lug was detected at the wrong position.
364 | HXX/AccBelt | 60215000 | Drive fault | The drive controller of this motor is reporting a fault condition.
365 | HXX/AccBelt | 60215001 | Position error | The controlled motor is out of the commanded position.
366 | HXX/AccBelt | 60215002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
367 | HXX/AccBelt | 60215003 | Validation fault | The module detected a value out of range.
368 | HXX/AccBelt | 60215004 | Switched off | The motor has been switched off temporarily.
369 | HXX/AccBelt | 60215008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
370 | HXX/AccBelt | 60215010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
371 | HXX/MetBelt | 60216000 | Drive fault | The drive controller of this motor is reporting a fault condition.
372 | HXX/MetBelt | 60216001 | Position error | The controlled motor is out of the commanded position.
373 | HXX/MetBelt | 60216002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
374 | HXX/MetBelt | 60216003 | Validation fault | The module detected a value out of range.
375 | HXX/MetBelt | 60216004 | Switched off | The motor has been switched off temporarily.
376 | HXX/MetBelt | 60216008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
377 | HXX/MetBelt | 60216010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
378 | HXX/MetBelt | 60216011 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
379 | HXX/Lng2 | 60222000 | Drive fault | The drive controller of this motor is reporting a fault condition.
380 | HXX/Lng2 | 60222001 | Position error | The controlled motor is out of the commanded position.
381 | HXX/Lng2 | 60222002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
382 | HXX/Lng2 | 60222003 | Validation fault | The module detected a value out of range.
383 | HXX/Lng2 | 60222004 | Switched off | The motor has been switched off temporarily.
384 | HXX/Lng2 | 60222008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
385 | HXX/Lng2 | 60222010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
386 | HXX/AxTopGuideBlt | 60224000 | Drive fault | The drive controller of this motor is reporting a fault condition.
387 | HXX/AxTopGuideBlt | 60224001 | Position error | The controlled motor is out of the commanded position.
388 | HXX/AxTopGuideBlt | 60224002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
389 | HXX/AxTopGuideBlt | 60224003 | Validation fault | The module detected a value out of range.
390 | HXX/AxTopGuideBlt | 60224004 | Switched off | The motor has been switched off temporarily.
391 | HXX/AxTopGuideBlt | 60224010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
392 | HXX/AxTopGuideBlt | 60224011 | Top guide belt not in working position | The top guide belt is not in working position.
393 | HXX/OpenCloseLng | 60230000 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
394 | HXX/LngVac | 60232000 | Drive fault | There is a fault on this drive.
395 | HXX/LngVac | 60232001 | Validation fault | The module detected a value out of range.
396 | HXX/LngVac | 60232002 | Circuit breaker | The circuit breaker for remove air at longitudinal sealing is switched off.
397 | HXX/AccProdInsp | 60255000 | Validation fault | The module detected a value out of range.
398 | HXX/AccProdInsp | 60255001 | Product too long | The product supervision detected a too long product in the infeed chain.
399 | HXX/AccProdInsp | 60255002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
400 | HXX/SRTransf | 60260001 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
401 | HXX/ProdInsp | 60262000 | Validation fault | The module detected a value out of range.
402 | HXX/ProdInsp | 60262001 | Product too long | The product supervision detected a too long product in the infeed chain.
403 | HXX/ProdInsp | 60262002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
404 | HXX/HighInsp | 60263000 | Validation fault | The module detected a value out of range.
405 | HXX/HighInsp | 60263001 | Product too high | The sensor which detects too high products has been activated.
406 | HXX/InfRej | 60264000 | Validation fault | The module detected a value out of range.
407 | HXX/InfRej | 60264001 | Too many products rejected over several cycles | Too many products were rejected continuously over several cycles.
408 | HXX/CrdBrdInsp | 60267000 | Validation fault | The module detected a value out of range.
409 | HXX/CrdBrdInsp | 60267001 | Cardboard too long | A cardboard in the infeed chain is too long or has jammed.
410 | HXX/CrdBrdInsp | 60267002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
411 | HXX/CrdBrdJam | 60268000 | Validation fault | The module detected a value out of range.
412 | HXX/CrdBrdJam | 60268001 | Jam | A cardboard in the infeed chain is too long or has jammed.
413 | HXX/CrdBrdJam | 60268002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
414 | HXX/AxChainSwitch | 60280000 | Drive fault | The drive controller of this motor is reporting a fault condition.
415 | HXX/AxChainSwitch | 60280001 | Position error | The controlled motor is out of the commanded position.
416 | HXX/AxChainSwitch | 60280002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
417 | HXX/AxChainSwitch | 60280003 | Validation fault | The module detected a value out of range.
418 | HXX/AxChainSwitch | 60280004 | Switched off | The motor has been switched off temporarily.
419 | HXX/AxChainSwitch | 60280007 | Brake manually released | The electrical brake of the chain switch motor is manually released.
420 | HXX/AxChainSwitch | 60280008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
421 | HXX/AxChainSwitch | 60280010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
422 | HXX/AxChainSwitch | 60280011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
423 | HXX/InfChain | 60285000 | No signal additional sensor | The additional proximity switch on the infeed chain did not detect any chain lug.
424 | HXX/AxSideGuide1 | 60298000 | Drive fault | The drive controller of this motor is reporting a fault condition.
425 | HXX/AxSideGuide1 | 60298001 | Position error | The controlled motor is out of the commanded position.
426 | HXX/AxSideGuide1 | 60298002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
427 | HXX/AxSideGuide1 | 60298003 | Validation fault | The module detected a value out of range.
428 | HXX/AxSideGuide1 | 60298004 | Switched off | The motor has been switched off temporarily.
429 | HXX/AxSideGuide1 | 60298010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
430 | HXX/AxSideGuide1 | 60298011 | Side guide belt not in working position | The side guide belt is not in working position.
431 | HXX/AxSideGuide2 | 60299000 | Drive fault | The drive controller of this motor is reporting a fault condition.
432 | HXX/AxSideGuide2 | 60299001 | Position error | The controlled motor is out of the commanded position.
433 | HXX/AxSideGuide2 | 60299002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
434 | HXX/AxSideGuide2 | 60299003 | Validation fault | The module detected a value out of range.
435 | HXX/AxSideGuide2 | 60299004 | Switched off | The motor has been switched off temporarily.
436 | HXX/AxSideGuide2 | 60299010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
437 | HXX/AxSideGuide2 | 60299011 | Side guide belt not in working position | The side guide belt is not in working position.
438 | HXX/FilmTrack | 60301000 | Home error | The homing of the film tracking control has not been successful.
439 | HXX/FilmTrack | 60301000 | Home error | The homing of the film tracking control has not been successful.
440 | HXX/FilmTrack | 60301001 | Homing active | The film tracking control is homing.
441 | HXX/FilmTrack | 60301001 | Homing active | The film tracking control is homing.
442 | HXX/FilmTrack | 60301002 | Not ready | The film tracking is not ready.
443 | HXX/FilmTrack | 60301002 | Not ready | The film tracking is not ready.
444 | HXX/FilmTrack | 60301003 | Film out of window | The film is not within the allowed window.
445 | HXX/FilmTrack | 60301003 | Film out of window | The film is not within the allowed window.
446 | HXX/FilmTrack | 60301010 | Film tracking sensor is dirty | Description: The film tracking sensor needs to be cleaned.
447 | HXX/FilmTrack | 60301010 | Film tracking sensor is dirty | Description: The film tracking sensor needs to be cleaned.
448 | HXX/FilmTrack | 60301013 | Circuit breaker film tracking | Description: The circuit breaker for the film tracking is switched off.
449 | HXX/FilmTrack | 60301013 | Circuit breaker film tracking | Description: The circuit breaker for the film tracking is switched off.
450 | HXX/Splicer | 60302000 | Add new roll of film | One film roll is empty.
451 | HXX/Splicer | 60302001 | Both film reels are empty | Both film reels are empty.
452 | HXX/SpliceInsp | 60307001 | Missing splice signal | There was a splice with a tape at inside of film which has to be detected with the splice supervision lightswitch. If there was no tape detected this fault occures
453 | HXX/NGNS | 60308000 | Validation fault | The module detected a value out of range.
454 | HXX/NGNS | 60308001 | No gap no seal detected over several cycles | No gap no seal has been detected continuously over several cycles.
455 | HXX/NGNS | 60308002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
456 | HXX/Printer | 60309000 | Message | The printer shows a message that does not lead to a machine stop (e.g. toner low).
457 | HXX/Printer | 60309001 | Not ready | The machine has been stopped due to an error of the printer.
458 | HXX/Printer | 60309002 | Circuit breaker | The printer circuit breaker is switched off.
459 | HXX/Printer | 60309003 | Filter Fault | The machine has been stopped due to an error of the printer filter.
460 | HXX/Printer | 60309004 | Filter Full | The Filter shows a message that the Filter is more than 75% full.
461 | HXX/Printer | 60309005 | Circuit breaker fume extractor | The fume extractor circuit breaker is switched off.
462 | HXX/SwiLev | 60317000 | Drive fault | The drive controller of this motor is reporting a fault condition.
463 | HXX/SwiLev | 60317003 | Validation fault | The module detected a value out of range.
464 | HXX/SwiLev | 60317011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
465 | HXX/SwiLev | 60317012 | Film is broken | The swingarm is at zero position.
466 | HXX/CutLengthMeas | 60318000 | Bad registration marks LS1 | A consecutive number of marks or flickers have been out of position. This could either mean that there are too many marks or that the sensor is flickering.
467 | HXX/CutLengthMeas | 60318001 | Bad registration marks LS2 | A consecutive number of marks or flickers have been out of position. This could either mean that there are too many marks or that the sensor is flickering.
468 | HPS | 60320001 | Splice process active | The splice process is active. The second roll is geared and both rolls are turning and synchronising. The splice process ends by cutting the film end and stopping the old roll. This is only an information.
469 | HPS | 60320002 | Emergency splice active | Emergency splice process is active. The button to do an emergency splice was activated. This process ends if the new roll is in place with its rape and the splicer arm is in splice position as well. This is only an information.
470 | HPS | 60320003 | New roll too small | The diameter of the new measured roll is too small. It's not worth to start running this roll.
471 | HPS | 60320004 | Check encoder wheel measuring arm | The encoder wheel of the measuring arm measured an invalid roll diameter.
472 | HPS | 60320005 | Mark on new roll not found | There was no registration mark found on the new roll.
473 | HPS | 60320006 | Tape on new roll not found | There was no tape found on the new roll.
474 | HPS | 60320007 | Wrong cut off length on new roll | The measured cut-off length is not compatible with the preset cut-off length on parameter values of the HMI. The mounted film roll is most probably the wrong one.
475 | HPS | 60320008 | Tape on cut position | The tape was detected on cut position. This leads to dirty knives at crosseal
476 | HPS | 60320010 | No new roll successfully prepared | There was no new roll loaded - or the loaded roll was bad.
477 | HPS | 60320011 | One roll empty | One film roll is empty.
478 | HPS | 60320013 | Simulation active | The simulation of the splice function is activated.
479 | HPS | 60320014 | Teach mode active | The teach mode is active. The machine won't start. With the jog button it is possible to move the measuring roll to teach the sensor to the registration mark or to the tape
480 | HPS | 60320015 | Check film | Check if the film is correctly threaded.
481 | HPS | 60320016 | Cut film manually needed | The knife is disabled. You need to cut the paper manually (after a desired adjusted lap length)
482 | HPS | 60320017 | Check splicer reg mark sensor | Something with this sensor is not ok (flickering, sees no product, ...). The machine will not stop because of this.
483 | HPS/Saf | 60321011 | Film roll access door open | There is an open door.
484 | HPS/Saf | 60321012 | Film roll access door open | There is an open door.
485 | HPS/Saf | 60321013 | Roll 1 mute switch fault | The mute switch to bypass the door is faulted.
486 | HPS/Saf | 60321014 | Roll 2 mute switch fault | The mute switch to bypass the door is faulted.
487 | HPS/Saf | 60321080 | Energize drives fault HPS | The energizing of the drives is faulted.
488 | HPS/Saf | 60321081 | Energize drives fault HPS Roll 1 | The energizing of the drives is faulted.
489 | HPS/Saf | 60321082 | Energize drives fault HPS Roll 2 | The energizing of the drives is faulted.
490 | HPS/Saf | 60321090 | Exhaust valve fault | The exhaust valve has a fault.
491 | HPS/Saf | 60321091 | Restarting exhaust valve | The exhaust valve is restarting.
492 | HPS/Saf | 60321092 | Energize exhaust valve fault | The energizing of the valve is faulted.
493 | HPS/Saf | 60321093 | Air pressure too low | The air pressure is below the allowed operating level.
494 | HPS/Saf | 60321094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
495 | HPS/Revolver | 60322000 | Drive fault | The drive controller of this motor is reporting a fault condition.
496 | HPS/Revolver | 60322001 | Position error | The controlled motor is out of the commanded position.
497 | HPS/Revolver | 60322002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
498 | HPS/Revolver | 60322003 | Validation fault | The module detected a value out of range.
499 | HPS/Revolver | 60322004 | Switched off | The motor has been switched off temporarily.
500 | HPS/Revolver | 60322007 | Brake manually released | The electrical brake of the cross seal motor is manually released.
501 | HPS/Revolver | 60322010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
502 | HPS/Revolver | 60322011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
503 | HPS/Roll1 | 60323000 | Drive fault | The drive controller of this motor is reporting a fault condition.
504 | HPS/Roll1 | 60323001 | Position error | The controlled motor is out of the commanded position.
505 | HPS/Roll1 | 60323002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
506 | HPS/Roll1 | 60323003 | Validation fault | The module detected a value out of range.
507 | HPS/Roll1 | 60323004 | Switched off | The motor has been switched off temporarily.
508 | HPS/Roll2 | 60324000 | Drive fault | The drive controller of this motor is reporting a fault condition.
509 | HPS/Roll2 | 60324001 | Position error | The controlled motor is out of the commanded position.
510 | HPS/Roll2 | 60324002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
511 | HPS/Roll2 | 60324003 | Validation fault | The module detected a value out of range.
512 | HPS/Roll2 | 60324004 | Switched off | The motor has been switched off temporarily.
513 | HPS/SwiLev | 60325000 | Drive fault | The drive controller of this motor is reporting a fault condition.
514 | HPS/SwiLev | 60325003 | Validation fault | The module detected a value out of range.
515 | HPS/SwiLev | 60325011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
516 | HPS/SwiLev | 60325012 | Film is broken | The swingarm is at zero position.
517 | HPS/Splicer | 60326000 | Drive fault | The drive controller of this motor is reporting a fault condition.
518 | HPS/Splicer | 60326001 | Position error | The controlled motor is out of the commanded position.
519 | HPS/Splicer | 60326002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
520 | HPS/Splicer | 60326003 | Validation fault | The module detected a value out of range.
521 | HPS/Splicer | 60326004 | Switched off | The motor has been switched off temporarily.
522 | HPS/Splicer | 60326007 | Motor brake manually released | The electrical brake of the cross seal motor is manually released.
523 | HPS/Splicer | 60326010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
524 | HPS/Splicer | 60326011 | Absolute position is not valid | The absolute position of the axis has been lost or never been taught.
525 | HPS/MeasArm | 60327000 | End switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
526 | HPS/MeasArm | 60327001 | Cylinder blocked | The end switch is still active, although the cyclinder was activated.
527 | HPS/EncMeasArm | 60328000 | Drive fault | The drive controller of this motor is reporting a fault condition.
528 | HPS/EncMeasArm | 60328003 | Validation fault | The module detected a value out of range.
529 | HPS/RollClamp | 60329000 | Clamp end switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
530 | HPS/RollClamp | 60329001 | Clamp cylinder blocked | The end switch is still active, although the cyclinder was activated.
531 | HPS/RollClamp | 60329002 | Stopper end switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
532 | HPS/RollClamp | 60329003 | Stopper cylinder blocked | The end switch is still active, although the cyclinder was activated.
533 | HPS/Knife | 60330000 | End switch fault | The end switch controls the position of this actuator. If the end switch has the wrong state compared to its controlled position then this fault is set.
534 | HPS/Knife | 60330001 | Cylinder blocked | The end switch is still active, although the cyclinder was activated.
535 | HXX/SAF | 60335035 | Cover printer open | There is a guard open.
536 | HXX/SAF | 60335036 | Printer not in work position | Printer is not in work position
537 | HXX/SAF | 60335081 | Energize printer fault | The energizing of the printer is faulted.
538 | HXX/OutfRej | 60350000 | Validation fault | The module detected a value out of range.
539 | HXX/OutfRej | 60350001 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
540 | HXX/OutfRej | 60350002 | Option to reject all products is enabled | The option to reject all products is enabled.
541 | HXX/OutfRejEmpty | 60351000 | Validation fault | The module detected a value out of range.
542 | HXX/OutfRejVerif | 60354000 | Validation fault | The module detected a value out of range.
543 | HXX/OutfRejVerif | 60354001 | Bad product was not rejected | The supervision of the outfeed rejection has detected a product that should have been rejected.
544 | HXX/OutfRejVerif | 60354002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will stop because of this.
545 | HXX/DoubleInsp | 60355000 | Validation fault | The module detected a value out of range.
546 | HXX/DoubleInsp | 60355001 | Double package rejected over several cycles | Double packages were rejected continuously over several cycles.
547 | HXX/DoubleInsp | 60355002 | Sensor not ok | Something with this sensor is not ok (flickering, sees no product, ...). The machine will stop because of this.
548 | HXX/OutfBeltVac | 60359000 | Circuit breaker | The circuit breaker is switched off.
549 | HXX/OutfBeltVac | 60359001 | Waiting for vacuum | The vacuum pump is starting up.
550 | HXX/OutfBeltVac | 60359002 | Drive fault | The drive controller of this motor is reporting a fault condition.
551 | HXX/OutfBeltVac | 60359003 | Validation fault | The module detected a value out of range.
552 | KA/VAxCrdBrd | 60500003 | Validation fault | The module detected a value out of range.
553 | KA/VAxCrdBrd | 60500008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
554 | KA/VAxCrdBrd | 60500011 | One cardboard reel empty | One of the two cardboard reels is emtpy.
555 | KA/VAxCrdBrd | 60500012 | Both cardboard reels are empty | Both cardboard reels are emtpy.
556 | KA/VAxCrdBrd | 60500013 | Cardboard reel empty | The cardboard reel is emtpy.
557 | KA/VAxCrdBrd | 60500015 | Message sup splice aktive | Message suplier splice aktive
558 | KA/VAxCrdBrd | 60500950 | Not displayed on HMI!
559 | KA/AxKnife | 60503000 | Drive fault | The drive controller of this motor is reporting a fault condition.
560 | KA/AxKnife | 60503001 | Position error | The controlled motor is out of the commanded position.
561 | KA/AxKnife | 60503002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
562 | KA/AxKnife | 60503003 | Validation fault | The module detected a value out of range.
563 | KA/AxKnife | 60503004 | Switched off | The motor has been switched off temporarily.
564 | KA/AxKnife | 60503006 | Proximity switch not found | During hard home procedure the home position could not been detected.
565 | KA/AxKnife | 60503008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
566 | KA/AxKnife | 60503010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
567 | KA/AxKnife | 60503011 | The top belt is not in working position | The top belt is not in working position
568 | KA/AxTrpUp | 60504000 | Drive fault | The drive controller of this motor is reporting a fault condition.
569 | KA/AxTrpUp | 60504001 | Position error | The controlled motor is out of the commanded position.
570 | KA/AxTrpUp | 60504002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
571 | KA/AxTrpUp | 60504003 | Validation fault | The module detected a value out of range.
572 | KA/AxTrpUp | 60504004 | Switched off | The motor has been switched off temporarily.
573 | KA/AxTrpUp | 60504010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
574 | KA/AxTrpUp | 60504011 | Cardboard jammed | The cardboard in the transport is jammed.
575 | KA/AxTrpLw | 60505000 | Drive fault | The drive controller of this motor is reporting a fault condition.
576 | KA/AxTrpLw | 60505001 | Position error | The controlled motor is out of the commanded position.
577 | KA/AxTrpLw | 60505002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
578 | KA/AxTrpLw | 60505003 | Validation fault | The module detected a value out of range.
579 | KA/AxTrpLw | 60505004 | Switched off | The motor has been switched off temporarily.
580 | KA/AxTrpLw | 60505010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
581 | KA/AxTrpLw | 60505011 | Cardboard jammed | The cardboard in the transport is jammed.
582 | KA/AxFeedChain | 60506000 | Drive fault | The drive controller of this motor is reporting a fault condition.
583 | KA/AxFeedChain | 60506001 | Position error | The controlled motor is out of the commanded position.
584 | KA/AxFeedChain | 60506002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
585 | KA/AxFeedChain | 60506003 | Validation fault | The module detected a value out of range.
586 | KA/AxFeedChain | 60506004 | Switched off | The motor has been switched off temporarily.
587 | KA/AxFeedChain | 60506006 | Proximity switch not found | During hard home procedure the home position could not been detected.
588 | KA/AxFeedChain | 60506008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
589 | KA/AxFeedChain | 60506010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
590 | KA/AxFeedChain | 60506011 | Top belt not in working position | The top belt after the knife is not in working position.
591 | KA/AxTrpCutBltUp | 60507000 | Drive fault | The drive controller of this motor is reporting a fault condition.
592 | KA/AxTrpCutBltUp | 60507001 | Position error | The controlled motor is out of the commanded position.
593 | KA/AxTrpCutBltUp | 60507002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
594 | KA/AxTrpCutBltUp | 60507003 | Validation fault | The module detected a value out of range.
595 | KA/AxTrpCutBltUp | 60507004 | Switched off | The motor has been switched off temporarily.
596 | KA/AxTrpCutBltUp | 60507008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
597 | KA/AxTrpCutBltUp | 60507010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
598 | KA/AxTrpCutBltLw | 60508000 | Drive fault | The drive controller of this motor is reporting a fault condition.
599 | KA/AxTrpCutBltLw | 60508001 | Position error | The controlled motor is out of the commanded position.
600 | KA/AxTrpCutBltLw | 60508002 | Servo output too high | The desired analog output to the servo drive is higher than 9.7V. With SERCOS application the maximum velocity of the Motor has been exceeded.
601 | KA/AxTrpCutBltLw | 60508003 | Validation fault | The module detected a value out of range.
602 | KA/AxTrpCutBltLw | 60508004 | Switched off | The motor has been switched off temporarily.
603 | KA/AxTrpCutBltLw | 60508008 | Motion instruction error | A motion instruction in command interpreter for home or maintenance has an error.
604 | KA/AxTrpCutBltLw | 60508010 | Home handler command not valid | The command interpreter for home or maintenance did not understand a command from the home handler or from the maintenance section of this module.
605 | H1 | 61009000 | Service mode active | The unit and the corresponding controlled leg belts are in Service mode. No rows will be distributed to this leg.
606 | H1 | 61009001 | Clean mode active | The unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
607 | H1 | 61009002 | Setup mode active | The unit and the corresponding controlled leg belts are in Setup mode. No rows will be distributed to this leg.
608 | H1 | 61009003 | Fill mode active | The unit and the corresponding controlled leg belts are in fill mode. No rows will be distributed to this leg.
609 | H1 | 61009004 | Empty mode active | The unit and the corresponding controlled leg belts are in clean mode. No rows will be distributed to this leg.
610 | H1 | 61009005 | Simulation mode active | The unit and the corresponding controlled leg belts are in simulation mode. No rows will be distributed to this leg.
611 | H1/Saf | 61021030 | Door machine outfeed open | There is a guard open.
612 | H1/Saf | 61021032 | Cover machine outfeed open | There is a guard open.
613 | H1/Saf | 61021033 | Cover folding box open | There is a guard open.
614 | H1/Saf | 61021034 | Door longitudinal sealing open | There is a guard open.
615 | H1/Saf | 61021035 | Cover printer open | There is a guard open.
616 | H1/Saf | 61021036 | Main cover open | There is a guard open.
617 | H1/Saf | 61021037 | Door After ejector Acceleration Belt open | There is a guard open.
618 | H1/Saf | 61021038 | Cover infeed chain open | There is a guard open.
619 | H1/Saf | 61021039 | Door Before ejector Acceleration Belt is open | There is a guard open.
620 | H1/Saf | 61021040 | Door metering belt open | There is a guard open.
621 | H1/Saf | 61021041 | Printer not in work position | Printer is not in work position
622 | H1/Saf | 61021043 | Door infeed chain mc side open | There is a guard open.
623 | H1/Saf | 61021044 | Door infeed chain middle open | There is a guard open.
624 | H1/Saf | 61021045 | Door infeed chain infeed side open | There is a guard open.
625 | H1/Saf | 61021046 | Cover infeed chain mc side open | There is a guard open.
626 | H1/Saf | 61021047 | Cover infeed chain middle open | There is a guard open.
627 | H1/Saf | 61021048 | Cover infeed chain infeed side open | There is a guard open.
628 | H1/Saf | 61021050 | Door control belt open | There is a guard open.
629 | H1/Saf | 61021051 | Door alignment belt open | There is a guard open.
630 | H1/Saf | 61021052 | Side alignment belt out of operating position | The alignment side belt is not in operating position.
631 | H1/Saf | 61021053 | Door turning belts open | There is a guard open.
632 | H1/Saf | 61021054 | Door after metal detector open | There is a guard open.
633 | H1/Saf | 61021055 | Door before metal detector open | There is a guard open.
634 | H1/Saf | 61021056 | Door alignment belt back open | There is a guard open.
635 | H1/Saf | 61021057 | Door after metal detector back open | There is a guard open.
636 | H1/Saf | 61021058 | Side guide rear side out of operating position | The side guide rear side is not in operating position.
637 | H1/Saf | 61021059 | Side guide front side out of operating position | The side guide front side is not in operating position.
638 | H1/Saf | 61021060 | Cover metering belt open | There is a guard open.
639 | H1/Saf | 61021061 | Cover control belt open | There is a guard open.
640 | H1/Saf | 61021062 | Door alignment belt mc side open | There is a guard open.
641 | H1/Saf | 61021063 | Door alignment belt middle open | There is a guard open.
642 | H1/Saf | 61021064 | Door alignment belt infeed side open | There is a guard open.
643 | H1/Saf | 61021065 | Door control belt mc side open | There is a guard open.
644 | H1/Saf | 61021066 | Door control belt middle open | There is a guard open.
645 | H1/Saf | 61021067 | Door control belt infeed side open | There is a guard open.
646 | H1/Saf | 61021068 | Door ejector Acceleration Belt open | There is a guard open.
647 | H1/Saf | 61021070 | Cover acceleration belt open | There is a guard open.
648 | H1/Saf | 61021074 | Door under curve chain open | There is a guard open.
649 | H1/Saf | 61021075 | Cover curve chain open | There is a guard open.
650 | H1/Saf | 61021080 | Energize drives fault HXX | The energizing of the drives is faulted.
651 | H1/Saf | 61021081 | Energize drives fault FXX | The energizing of the drives is faulted.
652 | H1/Saf | 61021082 | Energize drives fault Chain Switch | The energizing of the drives is faulted.
653 | H1/Saf | 61021085 | Energize drives fault Cab 1 | The energizing of the drives is faulted.
654 | H1/Saf | 61021086 | Energize drives fault Cab 2 | The energizing of the drives is faulted.
655 | H1/Saf | 61021087 | Energize drives fault Cab 3 | The energizing of the drives is faulted.
656 | H1/Saf | 61021090 | Exhaust valve fault | The exhaust valve has a fault.
657 | H1/Saf | 61021091 | Restarting exhaust valve | The exhaust valve is restarting.
658 | H1/Saf | 61021092 | Energize exhaust valve fault | The energizing of the valve is faulted.
659 | H1/Saf | 61021093 | Air pressure too low | The air pressure is below the allowed operating level.
660 | H1/Saf | 61021094 | Compressed air not exhausted | Even though the compressed air should have been exhausted due to an open safety circuit, the pressure monitor still reports compressed air in the system.
661 | H1/Saf | 61021100 | Door FBM open | There is a guard open.
662 | H1/Saf | 61021101 | Cover FBM open | There is a guard open.
663 | H1/Saf | 61021102 | Door FDM open | There is a guard open.
664 | H1/Saf | 61021103 | Cover FDM open | There is a guard open.
665 | H1/Saf | 61021110 | Door feeding wheel front side open | There is a guard open.
666 | H1/Saf | 61021111 | Door feeding wheel rear side open | There is a guard open.
667 | H1/Saf | 61021112 | Door feeding wheel infeed open | There is a guard open.
668 | H1/Saf | 61021113 | Door feeding wheel outfeed open | There is a guard open.
669 | H1/Saf | 61021120 | Door grouping chain open | There is a guard open.
670 | H1/Saf | 61021121 | Cover grouping chain open | There is a guard open.
671 | H1/Saf | 61021130 | Door folding box open | There is a guard open.
672 | H1/Saf | 61021130 | Door cardboard feeder open | There is a guard open.
673 | H1/Saf | 61021131 | Cover cardboard feeder open | There is a guard open.
674 | H1/Saf | 61021132 | Door cardboard chain open | There is a guard open.
675 | H1/Saf | 61021142 | Transport side belt 2 out of operating position | The transport side belt is not in operating position.
676 | H1/Saf | 61021143 | Transport side belt 3 out of operating position | The transport side belt is not in operating position.
677 | H1/Saf | 61021144 | Transport side belt 4 out of operating position | The transport side belt is not in operating position.
678 | H1/UIface | 61030000 | Ethernet communication fault with upstream | An ethernet fault with the upstream is active.
679 | H1/UIface | 61030001 | Interface signals overridden | The downstream interface signals are overridden
680 | H1/UIface | 61030002 | Upstream not ready | The upstream equipment is not ready.
681 | H1/DIface | 61031000 | Ethernet communication fault with downstream | An ethernet fault with the downstream is active.
682 | H1/DIface | 61031001 | Interface signals overridden | The downstream interface signals are overridden
683 | H1/DIface | 61031002 | Downstream not ready | The downstream equipment is not ready.
684 | H1/DIface | 61031003 | Check weigher not running or faulted | HCM is not allowed to produce to TTM before check weigher is running
685 | HPS | 61210000 | New roll is preparing for splice | This is a ready stop until the splice is prepared. The position of the working film roll is just before the splice - it is not allowed to run the machine until the preparation of the splice is completed.
686 | H1/OfdDvrt | 61901000 | Diverter in diverted position | The diverter at the downstream is in the diverted position.
687 | H1/OfdDvrt | 61901001 | Remove products from outfeed belt | Remove products from outfeed belt
688 | H1/OfdDvrt | 61901002 | Retail not ready | The switch is in the position RETAIL, but the retail is not ready.
689 | H1/OfdDvrt | 61901003 | Bulk not ready | The switch is in the position BULK, but the bulk is not ready.
690 | H1/OfdDvrt | 61901004 | Validation fault | The module detected a value out of range.
PLC 1 Data
Data# | Processor Tag |  | Value | Concentrator Tag | Path IP | Description | Python Variable Name
1 | [HCM274]HXX_SM_Iface.State.b_run |  | 1 | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.35 | Machine Running
2 | [HCM274]HXX_SM_Iface.Mode.b_production &not [HCM274]HXX_SM_iface.State.b_Alarm &not [HCM274]Ctrliface.b_running |  |  | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[0].1 | 10.168.100.35 | Machine Ready (Stopped)
3 | [HCM274]HXX_SM_Iface.Mode.b_production &not [HCM274]HXX_SM_iface.State.b_Alarm & [HCM274]Ctrliface.b_running &not [HCM274]HXX_SM_Iface.State.b_run |  |  | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[0].2 | 10.168.100.35 | Machine Ready (Waiting)
4 | [HCM274]HXX_SM_iface.State.b_Alarm |  | 1 | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[0].10 | 10.168.100.35 | Alarm Present
5 | [HCM274]HMI_Cmd.BtnEnShift1.b_Active |  | 1 | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[0].11 | 10.168.100.35 | Shift 1 Enabled
6 | [HCM274]HMI_Cmd.BtnEnShift2.b_Active |  | 1 | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[0].12 | 10.168.100.35 | Shift 2 Enabled
7 | [HCM274]HMI_Cmd.BtnEnShift3.b_Active |  | 1 | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[0].13 | 10.168.100.35 | Shift 3 Enabled
8 | [HCM274]HXX_SvAccProdInsp_HMI.Counter.dn_ProdWaste |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[9] | 10.168.100.35 | Pieces Rejected at Lug Chain | hcm_274_pieces_rejected_at_lug_chain
9 | [HCM274HXX_GLB_Iface.dn_ProdPerPack |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.35 | Pieces per Package | hcm_274_pieces_per_pack
10 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_PacksIn |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[11] | 10.168.100.35 | Packages into Wrapper | hcm_274_packages_into_wrapper
11 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_PacksWaste |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.35 | Packages Rejected Waste | hcm_274_packages_rejected_waste
12 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_PacksOut |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[13] | 10.168.100.35 | Packages Out From Wrapper | hcm_274_packs_out_from_wrapper
13 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_Double Pack |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[14] | 10.168.100.35 | Double Packages Rejected | hcm_274_double_packages_rejected
14 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_TooShortProd |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[15] | 10.168.100.35 | Packages Rejected Too Short | hcm_274_packages_rejected_too_short
15 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_TooLongProd |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[16] | 10.168.100.35 | Packages Rejected Too Long | hcm_274_packages_rejected_too_long
16 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_EmptyPack |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[17] | 10.168.100.35 | Packages Rejected Empty | hcm_274_packages_rejected_empty
17 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_OutOfRegist |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.35 | Packages Rejected Out of Registration | hcm_274_packages_rejected_out_of_registration
18 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_Splice |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.35 | Packages Rejected During Splice | hcm_274_packages_rejected_during_splice
19 | [HCM274]STA_Hmi.PresentShift.Performance_OfdRej.dn_SupSplice |  | Var | ComData_HCM_274_1_Alpha_To_Skynet.Status_Bits[20] | 10.168.100.35 | Packages Rejected Supplier Splice | hcm_274_packages_rejected_supplier_splice
20 | [HCM273]STA_Hmi.PresentShift.OEE.r_OEE |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Process_Values[10] |  | OEE | hcm_274_oee
21 | [HCM273]STA_Hmi.PresentShift.OEE.r_Availability |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Process_Values[11] |  | Availability | hcm_274_avail
22 | [HCM273]STA_Hmi.PresentShift.Performance_Mc.r_PacksPerMinute |  |  | ComData_HCM_273_1_Alpha_To_Skynet.Process_Values[13] |  | Bars per Minute | hcm_274_bars_min_out
10 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdIn |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[13] | 10.168.100.35 | Pieces received at 3D Profile Station
11 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdWaste |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[14] | 10.168.100.35 | Total of rejected Pieces at 3D Profile
12 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdOut |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[15] | 10.168.100.35 | Product count ater 3D Profile
13 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooLong |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[16] | 10.168.100.35 | Rejected Count for Too Long
14 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooHigh |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[17] | 10.168.100.35 | Rejected Count for Too High
15 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooWide |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.35 | Rejected Count for Too Wide
16 | [HCM274]HXX_InfRej_Hmi.counter.dn_ProdWaste |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.35 | Rows Distributed into Buffer
17 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooShort |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[20] | 10.168.100.35 | Rows Distributed to Wrapping Leg 1
18 | [HCM274]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooShort |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[21] | 10.168.100.35 | Rows Distributed to Wrapping Leg 2
19 | [HCM274]DA_Ctr_Iface.dn_FillingLevelPercent |  | Var | ComData_HCM_274_Alpha_To_Skynet.Status_Bits[22] | 10.168.100.35 | Buffer Fill Level
20 | [HCM274]HMI_Cmd.Dn_StartHoursShift1 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[0] | 10.168.100.35 | Start Time Hours Shift 1
21 | [HCM274]HMI_Cmd.Dn_StartMinutesShift1 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[1] | 10.168.100.35 | Start Time Minutes Shift 1
22 | [HCM274]HMI_Cmd.Dn_StartHoursShift2 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[2] | 10.168.100.35 | Start Time Hours Shift 2
23 | [HCM274]HMI_Cmd.Dn_StartMinutesShift2 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[3] | 10.168.100.35 | Start Time Minutes Shift 2
24 | [HCM274]HMI_Cmd.Dn_StartHoursShift3 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[4] | 10.168.100.35 | Start Time Hours Shift 3
25 | [HCM274]HMI_Cmd.Dn_StartMinutesShift3 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[5] | 10.168.100.35 | Start Time Minutes Shift 3
26 | [HCM274]HMI_Cmd.Dn_EndHoursShift1 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[6] | 10.168.100.35 | End Time Hours Shift 1
27 | [HCM274]HMI_Cmd.Dn_EndMinutesShift1 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[7] | 10.168.100.35 | End Time Minutes Shift 1
28 | [HCM274]HMI_Cmd.Dn_EndHoursShift2 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[8] | 10.168.100.35 | End Time Hours Shift 2
29 | [HCM274]HMI_Cmd.Dn_EndMinutesShift2 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[9] | 10.168.100.35 | End Time Minutes Shift 2
30 | [HCM274]HMI_Cmd.Dn_EndHoursShift3 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[10] | 10.168.100.35 | End Time Hours Shift 3
31 | [HCM274]HMI_Cmd.Dn_EndMinutesShift3 |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[11] | 10.168.100.35 | End Time Minutes Shift 3
32 | [HCM274]HMI_dn_Hour |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[12] | 10.168.100.35 | Current Hour In Processor
33 | [HCM274]HMI_dn_Minute |  | Var | ComData_HCM_274_Alpha_To_Skynet.Parameters[13] | 10.168.100.35 | Current Minute In Processor
34 | [HCM274]SM.Errors.DynText.List[0].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[0] | 10.168.100.35 | Dynamic Text Fault List 0
35 | [HCM274]SM.Errors.DynText.List[1].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[1] | 10.168.100.35 | Dynamic Text Fault List 1
36 | [HCM274]SM.Errors.DynText.List[2].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[2] | 10.168.100.35 | Dynamic Text Fault List 2
37 | [HCM274]SM.Errors.DynText.List[3].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[3] | 10.168.100.35 | Dynamic Text Fault List 3
38 | [HCM274]SM.Errors.DynText.List[4].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[4] | 10.168.100.35 | Dynamic Text Fault List 4
39 | [HCM274]SM.Errors.DynText.List[5].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[5] | 10.168.100.35 | Dynamic Text Fault List 5
40 | [HCM274]SM.Errors.DynText.List[6].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[6] | 10.168.100.35 | Dynamic Text Fault List 6
41 | [HCM274]SM.Errors.DynText.List[7].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[7] | 10.168.100.35 | Dynamic Text Fault List 7
42 | [HCM274]SM.Errors.DynText.List[8].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[8] | 10.168.100.35 | Dynamic Text Fault List 8
43 | [HCM274]SM.Errors.DynText.List[9].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[9] | 10.168.100.35 | Dynamic Text Fault List 9
44 | [HCM274]SM.Errors.FixText.List[0].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[30] | 10.168.100.35 | Fixed Text Fault List 0
45 | [HCM274]SM.Errors.FixText.List[1].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[31] | 10.168.100.35 | Fixed Text Fault List 1
46 | [HCM274]SM.Errors.FixText.List[2].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[32] | 10.168.100.35 | Fixed Text Fault List 2
47 | [HCM274]SM.Errors.FixText.List[3].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[33] | 10.168.100.35 | Fixed Text Fault List 3
48 | [HCM274]SM.Errors.FixText.List[4].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[34] | 10.168.100.35 | Fixed Text Fault List 4
49 | [HCM274]SM.Errors.FixText.List[5].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[35] | 10.168.100.35 | Fixed Text Fault List 5
50 | [HCM274]SM.Errors.FixText.List[6].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[36] | 10.168.100.35 | Fixed Text Fault List 6
51 | [HCM274]SM.Errors.FixText.List[7].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[37] | 10.168.100.35 | Fixed Text Fault List 7
52 | [HCM274]SM.Errors.FixText.List[8].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[38] | 10.168.100.35 | Fixed Text Fault List 8
53 | [HCM274]SM.Errors.FixText.List[9].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[39] | 10.168.100.35 | Fixed Text Fault List 9
54 | [HCM274]SM.Errors.FixText.List[10].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[40] | 10.168.100.35 | Fixed Text Fault List 10
55 | [HCM274]SM.Errors.FixText.List[11].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[41] | 10.168.100.35 | Fixed Text Fault List 11
56 | [HCM274]SM.Errors.FixText.List[12].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[42] | 10.168.100.35 | Fixed Text Fault List 12
57 | [HCM274]SM.Errors.FixText.List[13].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[43] | 10.168.100.35 | Fixed Text Fault List 13
58 | [HCM274]SM.Errors.FixText.List[14].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[44] | 10.168.100.35 | Fixed Text Fault List 14
59 | [HCM274]SM.Errors.FixText.List[15].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[45] | 10.168.100.35 | Fixed Text Fault List 15
60 | [HCM274]SM.Errors.FixText.List[16].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[46] | 10.168.100.35 | Fixed Text Fault List 16
61 | [HCM274]SM.Errors.FixText.List[17].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[47] | 10.168.100.35 | Fixed Text Fault List 17
62 | [HCM274]SM.Errors.FixText.List[18].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[48] | 10.168.100.35 | Fixed Text Fault List 18
63 | [HCM274]SM.Errors.FixText.List[19].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[49] | 10.168.100.35 | Fixed Text Fault List 19
64 | [HCM274]SM.Errors.FixText.List[20].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[50] | 10.168.100.35 | Fixed Text Fault List 20
65 | [HCM274]SM.Errors.FixText.List[21].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[51] | 10.168.100.35 | Fixed Text Fault List 21
66 | [HCM274]SM.Errors.FixText.List[22].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[52] | 10.168.100.35 | Fixed Text Fault List 22
67 | [HCM274]SM.Errors.FixText.List[23].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[53] | 10.168.100.35 | Fixed Text Fault List 23
68 | [HCM274]SM.Errors.FixText.List[24].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[54] | 10.168.100.35 | Fixed Text Fault List 24
69 | [HCM274]SM.Errors.FixText.List[25].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[55] | 10.168.100.35 | Fixed Text Fault List 25
70 | [HCM274]SM.Errors.FixText.List[26].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[56] | 10.168.100.35 | Fixed Text Fault List 26
71 | [HCM274]SM.Errors.FixText.List[27].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[57] | 10.168.100.35 | Fixed Text Fault List 27
72 | [HCM274]SM.Errors.FixText.List[28].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[58] | 10.168.100.35 | Fixed Text Fault List 28
73 | [HCM274]SM.Errors.FixText.List[29].dn_ID |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[59] | 10.168.100.35 | Fixed Text Fault List 29
74 | [HCM274]SM.Errors.DynText.dn_LastPos |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[60] | 10.168.100.35 | Position of Last stored position in Dyn List
75 | [HCM274]SM.Errors.FixText.dn_LastPos |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[61] | 10.168.100.35 | Position of Last stored position in Fix List
76 | [HCM274]SM.Errors.DynText.dn_EmptyPos |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[62] | 10.168.100.35 | Position of Next stored position in Dyn List
77 | [HCM274]SM.Errors.FixText.dn_EmptyPos |  | Var | ComData_HCM_274_Alpha_To_Skynet.Fault_data[63] | 10.168.100.35 | Position of Next stored position in Fix List
PLC 2 Data
1 | [HCM274]UIFace_DXX_OUT.b_ready |  | 1 | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.35 | FXX Infeed Running
2 | [HCM274]STA_Hmi.PresentShift.Performance_MetalRej.dn_ProdIn |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.35 | Pieces Received at Metal Detector | hcm_274_pieces_received_at_metal_detector
3 | [HCM274]STA_Hmi.PresentShift.Performance_MetalRej.dn_ProdWaste |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[11] | 10.168.100.35 | Rejected Count for Metal Detector
4 | [HCM274]STA_Hmi.PresentShift.Performance_MetalRej.dn_ProdOut |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.35 | Pieces Passed Metal Detector | hcm_274_pieces_passed_metal_detector
5 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdIn |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[13] | 10.168.100.35 | Pieces Received at 3D Profile Station | hcm_274_pieces_received_at_3d_profile_station
6 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdTooLong |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[14] | 10.168.100.35 | Rejected Count for Too Long | hcm_274_rejected_count_for_too_long
7 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdTooShort |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[15] | 10.168.100.35 | Rejected Count for Too Short | hcm_274_rejected_count_for_too_short
8 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdTooHigh |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[16] | 10.168.100.35 | Rejected Count for Too High | hcm_274_rejected_count_for_too_high
9 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdToowide |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[17] | 10.168.100.35 | Rejected Count for Too Wide | hcm_274_rejected_count_for_too_wide
10 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_GapTooSmall |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.35 | Rejected Count for Gap Too Small | hcm_274_rejected_count_for_gap_too_small
11 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdWaste |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.35 | Total of Rejected Pieces at 3D Profile | hcm_274_total_of_rejected_pieces_at_3d_profile
12 | [HCM274]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdOut |  | Var | ComData_HCM_274_2_Alpha_To_Skynet.Status_Bits[20] | 10.168.100.35 | Pieces Passed 3D Profile Station | hcm_274_pieces_passed__3d_profile_station

## Alpha TTM 147
HMI Fault Messages:
# | Component | Fault Value | Error Text | Description
CLO1
1 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.208.008 | Actual position Tool Center Point (TCP) out of range | The actual position of the Tool Center Point (TCP) is outside of the allowed working range
2 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.208.010 | Command Position Tool Center Point (TCP) out of range | The command position of the Tool Center Point (TCP) is outside of the allowed working range
3 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.208.011 | Actual position Tool Center Point (TCP) out of range | The actual position of the Tool Center Point (TCP) is outside of the allowed working range
4 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.001 | Excessive error on Tool Center Point (TCP) | The allowed difference between two program scans to large.
5 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.002 | Actual position Joint 4 (P4) out of range | The actual position of Joint 4 (P4) is outside of the allowed working range
6 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.003 | Command Position Joint 4 (P4) out of range | The command position of Joint 4 (P4) is outside of the allowed working range
7 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.004 | Actual position Joint 4 (P4) out of range | The actual position of Joint 4 (P4) is outside of the allowed working range
8 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.010 | Excessive error on Position Joint 4 (P4) | The allowed difference between two program scans to large.
9 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.011 | Excessive error on Joint 2 | The allowed difference between two program scans to large.
10 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.012 | Excessive error on Joint 3 | The allowed difference between two program scans to large.
11 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.013 | Excessive error on Joint 4 | The allowed difference between two program scans to large.
12 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.300.014 | Absolute Position Error | A position which has to be absolute is defined as relative position
13 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.001 | Relative Position Error | No absolute reference position is defined for relative positions
14 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.002 | Repos of robot required | Repositioning of Robot required
15 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.005 | Absolute position not in working area : | An absolute position is outside the defined working area
16 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.006 | Working area error | The working area of P4 is bigger than the frame size
17 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.007 | Motion Instruction Error | Motion Instruction Error in the software
18 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.008 | Routine Stop Timeout | Routine Stop Timeout in the software
19 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.009 | Routine Termination Timeout | Routine Termination Timeout in the software
20 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.010 | Joint 2 torque to hight : | Torque higher than allowed limit for the gear box
21 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.011 | Joint 3 torque to hight : | Torque higher than allowed limit for the gear box
22 | [TTM147-3]CLO1_RBT1Evt_ErrIface..b_Display | 74.302.012 | Joint 4 torque to hight : | Torque higher than allowed limit for the gear box
23 | #N/A | 74.302.013
24 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.014 | Motion Instruction Error | Motion Instruction Error in the software
25 | #N/A | 74.302.015
26 | [TTM147-3]CLO1_GRC1_ErrIface..b_Display | 74.302.016 | Gripper crashed | Description : The Gripper collided with something
27 | [TTM147-3]CLO1_GRC1_ErrIface..b_Display | 74.302.017 | Gripper not connected | Description : No gripper installed or gripper not locked
28 | [TTM147-3]CLO1_GRC1_ErrIface..b_Display | 74.302.018 | Wrong gripper installed | Description : Disagreement between the input gripper code and the gripper code from the recipe parameters
29 | [TTM147-3]CLO1_GRC1_ErrIface..b_Display | 74.302.019 | Gripper network fault | Description : The gripper network is interrupted.
30 | #N/A | 74.302.020
31 | [TTM147-3]CLO1_GLU1_ErrIface..b_Display | 74.302.021 | Hotmelt-Alarm | GLU Unit General Alarm
32 | [TTM147-3]CLO1_GLU1_ErrIface..b_Display | 74.302.022 | Hotmelt level too low | Hotmelt level too low
33 | [TTM147-3]CLO1_GLU1_ErrIface..b_Display | 74.302.023 | Glue unit not ready | Glue Unit not ready in ServiceMode (Info)
34 | [TTM147-3]CLO1_GLU1_ErrIface..b_Display | 74.302.030 | Glue unit not ready | Glue Unit not ready in ProdMode
35 | #N/A | 74.302.031
36 | [TTM147-3]CLO1_SM_ErrIface.b_StateTimeout.b_Display | 74.302.032 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
37 | [TTM147-3]CLO1_SM_ErrIface.b_ServiceModeActive.b_Display | 74.302.033 | Service mode active | The machine part is in service mode.
38 | [TTM147-3]CLO1_SM_ErrIface.b_CalculationActive.b_Display | 74.302.034 | Calculation active | The unit is in calculation state.
39 | [TTM147-3]CLO1_SM_ErrIface.b_StateMachineDisabled.b_Display | 74.302.035 | Switched off | This machine part is disabled
40 | [TTM147-3]CLO1_SM_ErrIface.b_ActivatingPwrFault.b_Display | 74.302.036 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
41 | #N/A | 74.302.037
42 | [TTM147-3]CLO1_DH_ErrIface..b_Display | 74.302.050 | Decel Not Finished In Time: | The Decelhandler wasn't able to finish in the requested time
43 | #N/A | 74.302.051
44 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.052 | Drive Fault Axis 2: | The drive of axis 2 is in fault state
45 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.053 | Axis 2 not enabled | Axis 2 not enabled
46 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.054 | Axis 2 not Calibrated | Axis 2 is not calibrated
47 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.055 | Limit Warning Axis 2 | Axis 2 has excessed a software or hardware limit
48 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.056 | Software Limit Fault Axis 2 | Axis 2 has excessed a software limit
49 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.057 | Hardware Limit Fault Axis 2 | Axis 2 has excessed a hardware limit
50 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.058 | Axis 2 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
51 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.059 | Brake released Axis 2 | The mechanical brake of axis 2 was released manually
52 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.060 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
53 | #N/A | 74.302.061
54 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.062 | Drive Fault Axis 3: | The drive of axis 3 is in fault state
55 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.070 | Axis 3 not enabled | Axis 3 not enabled
56 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.071 | Axis 3 not Calibrated | Axis 3 is not calibrated
57 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.072 | Limit Warning Axis 3 | Axis 3 has excessed a software or hardware limit
58 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.073 | Software Limit Fault Axis 3 | Axis 3 has excessed a software limit
59 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.074 | Hardware Limit Fault Axis 3 | Axis 3 has excessed a hardware limit
60 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.075 | Axis 3 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
61 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.090 | Brake released Axis 3 | The mechanical brake of axis 3 was released manually
62 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.091 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
63 | #N/A | 74.302.092
64 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.093 | Drive Fault Axis 4: | The drive of axis 4 is in fault state
65 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.094 | Axis 4 not enabled | Axis 4 not enabled
66 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.095 | Axis 4 not Calibrated | Axis 4 is not calibrated
67 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.096 | Limit Warning Axis 4 | Axis 4 has excessed a software or hardware limit
68 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.097 | Software Limit Fault Axis 4 | Axis 4 has excessed a software limit
69 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.098 | Hardware Limit Fault Axis 4 | Axis 4 has excessed a hardware limit
70 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.099 | Axis 4 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
71 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.100 | Brake released Axis 4 | The mechanical brake of axis 4 was released manually
72 | [TTM147-3]CLO1_RBT1Slw_ErrIface..b_Display | 74.302.101 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
FOR1 |  | 74.302.102
73 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.302.120 | Actual position Tool Center Point (TCP) out of range | The actual position of the Tool Center Point (TCP) is outside of the allowed working range
74 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.302.121 | Command position Tool Center Point (TCP) out of range | The command position of the Tool Center Point (TCP) is outside of the allowed working range
75 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.302.122 | Actual position Tool Center Point (TCP) out of range | The actual position of the Tool Center Point (TCP) is outside of the allowed working range
76 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.302.123 | Excessive error on Tool Center Point (TCP) | The allowed difference between two program scans to large.
77 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.302.124 | Actual position Joint 4 (P4) out of range | The actual position of Joint 4 (P4) is outside of the allowed working range
78 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.304.001 | Command position Joint 4 (P4) out of range | The command position of Joint 4 (P4) is outside of the allowed working range
79 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.304.002 | Actual position Joint 4 (P4) out of range | The actual position of Joint 4 (P4) is outside of the allowed working range
80 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.304.003 | Excessive error on position Joint 4 (P4) | The allowed difference between two program scans to large.
81 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.304.004 | Excessive error on Joint 2 | The allowed difference between two program scans to large.
82 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.304.005 | Excessive error on Joint 3 | The allowed difference between two program scans to large.
83 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.304.006 | Excessive error on Joint 4 | The allowed difference between two program scans to large.
84 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.305.001 | Absolute position Error | A position which has to be absolute is defined as relative position
85 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.305.002 | Relative position Error | No absolute reference position is defined for relative positions
86 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.305.003 | Repos of robot required | Repositioning of Robot required
87 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.305.004 | Absolute position not in working area | An absolute position is outside the defined working area
88 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.010 | Working area error | The working area of P4 is bigger than the frame size
89 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.011 | Motion Instruction Error | Motion Instruction Error in the software
90 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.012 | Routine stop timeout | Routine Stop Timeout in the software
91 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.013 | Routine termination timeout | Routine Termination Timeout in the software
92 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.014 | Joint 2 torque to hight : | Torque higher than allowed limit for the gear box
93 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.015 | Joint 3 torque to hight : | Torque higher than allowed limit for the gear box
94 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.016 | Joint 4 torque to hight : | Torque higher than allowed limit for the gear box
95 | [TTM147-3]FOR1_RBT1Evt_ErrIface..b_Display | 74.401.017 | Neighbouring robot out of range | Neighbouring robot is out of the defined working range and this raises the risc of a collision
96 | #N/A | 74.401.018
97 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 74.401.020 | Motion Instruction Error | Motion Instruction Error in the software
98 | #N/A | 74.401.023
99 | [TTM147-3]FOR1_GRF1_ErrIface..b_Display | 75.231.001 | Gripper not connected | No gripper installed or gripper not locked
100 | [TTM147-3]FOR1_GRF1_ErrIface..b_Display | 75.231.002 | Wrong gripper installed | Disagreement between the input gripper code and the gripper code from the recipe parameters
101 | [TTM147-3]FOR1_GRF1_ErrIface..b_Display | 75.231.005 | Vacuum Error | Vacuum Error on Gripper
102 | [TTM147-3]FOR1_GRF1_ErrIface..b_Display | 75.231.003 | Pick-Position sensor fault | Gripper turn-sensor feedback not match
103 | [TTM147-3]FOR1_GRF1_ErrIface..b_Display | 75.231.004 | Place-Position sensor fault | Gripper turn-sensor feedback not match
104 | #N/A | 75.234.002
105 | [TTM147-3]FOR1_GLU1_ErrIface..b_Display | 75.234.003 | Hotmelt-Alarm | GLU Unit General Alarm
106 | [TTM147-3]FOR1_GLU1_ErrIface..b_Display | 75.234.004 | Hotmelt level too low | Hotmelt level too low
107 | [TTM147-3]FOR1_GLU1_ErrIface..b_Display | 75.234.005 | Glue unit not ready | Glue Unit not ready in ServiceMode (Info)
108 | [TTM147-3]FOR1_GLU1_ErrIface..b_Display | 75.234.006 | Glue unit not ready | Glue Unit not ready in ProdMode
109 | #N/A | 75.234.007
110 | [TTM147-3]FOR1_BLT1Evt_ErrIface..b_Display | 75.234.008 | Motion Instruction Error | Motion Instruction Error in the software
111 | [TTM147-3]FOR1_BLT1Evt_ErrIface..b_Display | 75.234.009 | Routine Stop Timeout | Routine Stop Timeout in the software
112 | [TTM147-3]FOR1_BLT1Evt_ErrIface..b_Display | 75.234.010 | Routine Termination Timeout | Routine Termination Timeout in the software
113 | [TTM147-3]FOR1_BLT1Evt_ErrIface..b_Display | 75.234.023 | Glued Blank Timeout - open door and remove blanks | A glued blank was not formed in time
114 | [TTM147-3]FOR1_BLT1Slw_ErrIface..b_Display | 75.234.027 | Drive Fault Axis BLT: | The drive of axis BLT is in fault state
115 | [TTM147-3]FOR1_BLT1Slw_ErrIface..b_Display | 75.234.030 | PositionError Axis BLT | Axis BLt has excessed the allowed position error
116 | [TTM147-3]FOR1_BLT1Slw_ErrIface..b_Display | 75.234.031 | Software Limit Fault Axis BLT | Axis BLT has excessed a software limit
117 | [TTM147-3]FOR1_BLT1Slw_ErrIface..b_Display | 75.234.032 | Software Limit Warning Axis BLT | Axis BLT has excessed a software limit
118 | [TTM147-3]FOR1_BLT1Slw_ErrIface..b_Display | 75.234.033 | Axis BLT not Calibrated | Axis BLT is not calibrated
119 | [TTM147-3]FOR1_BLT1Slw_ErrIface..b_Display | 75.234.034 | Motion Instruction Error | Motion Instruction Error in the software
120 | #N/A | 75.234.035
121 | [TTM147-3]FOR1_BLP1Evt_ErrIface..b_Display | 75.234.036 | Vacuum Error - open door and remove blanks | Blank not picked
122 | [TTM147-3]FOR1_BLP1Evt_ErrIface..b_Display | 75.234.037 | Motion Instruction Error | Motion Instruction Error in the software
123 | [TTM147-3]FOR1_BLP1Evt_ErrIface..b_Display | 75.234.038 | Routine Stop Timeout | Routine Stop Timeout in the software
124 | [TTM147-3]FOR1_BLP1Evt_ErrIface..b_Display | 75.234.039 | Routine Termination Timeout | Routine Termination Timeout in the software
125 | [TTM147-3]FOR1_BLP1Evt_ErrIface..b_Display | 75.234.040 | Vacuum Error Switch | Vacuum switch is allways ON.
126 | [TTM147-3]FOR1_BLP1Evt_ErrIface..b_Display | 75.234.041 | BLP not in Home Position | BLP is not in Home Position. Gripper change not possible
127 | [TTM147-3]FOR1_BLP1Evt_ErrIface..b_Display | 75.234.042 | Blank allocation error | The subbatch expected by the VTT does not match with the actual allocation of blanks on the blank transport
128 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.043 | Drive Fault Axis BLP: | The drive of axis BLP is in fault state
129 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.044 | PositionError Axis BLP | Axis BLP has excessed the allowed position error
130 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.045 | Software Limit Fault Axis BLP | Axis BLP has excessed a software limit
131 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.046 | Software Limit Warning Axis BLP | Axis BLP has excessed a software limit
132 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.047 | Axis BLP not Calibrated | Axis BLP is not calibrated
133 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.048 | Axis BLP BrakeReleased | Axis BLP not in closed loop and brake released
134 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.049 | Motion Instruction Error | Motion Instruction Error in the software
135 | [TTM147-3]FOR1_BLP1Slw_ErrIface..b_Display | 75.234.050 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
136 | #N/A | 75.234.051
137 | [TTM147-3]FOR1_BLM1_ErrIface..b_Display | 75.234.052 | Magazine low level | The blank magazine reached the low level (left sensor)
138 | [TTM147-3]FOR1_BLM1_ErrIface..b_Display | 75.234.053 | Magazine is empty | The blank magazine reached the empty level (right sensor)
139 | [TTM147-3]FOR1_BLM1_ErrIface..b_Display | 75.234.054 | Transport fault | The cylinder is not able to tranpsort blanks to the pick position
140 | [TTM147-3]FOR1_BLM1_ErrIface..b_Display | 75.234.055 | Assembling fault | The blank magazine isn't assembled correct
141 | [TTM147-3]FOR1_BLM1_ErrIface..b_Display | 75.234.056 | Blanks not ready | The blanks in the magazine are not ready to be picked
142 |  | 75.234.057
143 | [TTM147-3]FOR1_SM_ErrIface.b_StateTimeout.b_Display | 75.234.058 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
144 | [TTM147-3]FOR1_SM_ErrIface.b_ServiceModeActive.b_Display | 75.234.059 | Service mode active | The machine part is in service mode.
145 | [TTM147-3]FOR1_SM_ErrIface.b_CalculationActive.b_Display | 75.234.060 | Calculation active | The unit is in calculation state.
146 | [TTM147-3]FOR1_SM_ErrIface.b_StateMachineDisabled.b_Display | 75.234.061 | Switched off | This machine part is disabled
147 | [TTM147-3]FOR1_SM_ErrIface.b_ActivatingPwrFault.b_Display | 75.234.062 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
148 | #N/A | 75.234.100
149 | [TTM147-3]FOR1_DH_ErrIface..b_Display | 75.234.107 | Decel Not Finished In Time: | The Decelhandler wasn't able to finish in the requested time
150 | #N/A | 75.234.108
151 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.120 | Drive Fault Axis 2: | The drive of axis 2 is in fault state
152 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.128 | Axis 2 not enabled | Axis 2 not enabled
153 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.140 | Axis 2 not Calibrated | Axis 2 is not calibrated
154 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.147 | Limit Warning Axis 2 | Axis 2 has excessed a software or hardware limit
155 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.148 | Software Limit Fault Axis 2 | Axis 2 has excessed a software limit
156 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.149 | Hardware Limit Fault Axis 2 | Axis 2 has excessed a hardware limit
157 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.180 | Axis 2 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
158 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.184 | Brake released Axis 2 | The mechanical brake of axis 2 was released manually
159 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.187 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
160 | #N/A | 75.234.188
161 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.190 | Drive Fault Axis 3: | The drive of axis 3 is in fault state
162 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.191 | Axis 3 not enabled | Axis 3 not enabled
163 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.192 | Axis 3 not Calibrated | Axis 3 is not calibrated
164 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.193 | Limit Warning Axis 3 | Axis 3 has excessed a software or hardware limit
165 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.194 | Software Limit Fault Axis 3 | Axis 3 has excessed a software limit
166 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.200 | Hardware Limit Fault Axis 3 | Axis 3 has excessed a hardware limit
167 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.201 | Axis 3 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
168 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.204 | Brake released Axis 3 | The mechanical brake of axis 3 was released manually
169 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.207 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
170 | #N/A | 75.234.208
171 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.210 | Drive Fault Axis 4: | The drive of axis 4 is in fault state
172 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.211 | Axis 4 not enabled | Axis 4 not enabled
173 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.212 | Axis 4 not Calibrated | Axis 4 is not calibrated
174 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.213 | Limit Warning Axis 4 | Axis 4 has excessed a software or hardware limit
175 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.214 | Software Limit Fault Axis 4 | Axis 4 has excessed a software limit
176 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.260 | Hardware Limit Fault Axis 4 | Axis 4 has excessed a hardware limit
177 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.267 | Axis 4 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
178 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.268 | Brake released Axis 4 | The mechanical brake of axis 4 was released manually
179 | [TTM147-3]FOR1_RBT1Slw_ErrIface..b_Display | 75.234.270 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
GEN1 |  | 75.234.271
| PLC1 | 75.234.272
180 | [TTM147-1]PLC1_CPU_ErrIface..b_Display | 75.234.273 | Missing Remote IO | Missing Remote IO
181 | [TTM147-1]PLC1_CPU_ErrIface..b_Display | 75.234.274 | Routine Termination Time Out | The modul wasn't able to execute the procedure in the requested time
182 | [TTM147-1]PLC1_CPU_ErrIface..b_Display | 75.234.280 | HMI Communication Error | The Communication to the HMI is not ok
183 | [TTM147-1]PLC1_CPU_ErrIface..b_Display | 75.234.284 | Task overlap occured | CPU usage is very high
184 | [TTM147-1]PLC1_CPU_ErrIface..b_Display | 75.234.287 | Task overlaps occured | CPU usage is very high
185 | #N/A | 75.234.288
186 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.290 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
187 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.291 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
188 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.292 | Too small | This is a system failure: the shown registration list is too small.
189 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.293 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
190 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.294 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
191 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.300 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
192 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.301 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
193 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.304 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
194 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.307 | Controller Timeout | Global Statemachine fault.
195 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.308 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
196 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.310 | State machine init - | This is a system failure.
197 | [TTM147-1]PLC1_SM_Ctr_ErrIface..b_Display | 75.234.311 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
198 | #N/A | 75.234.312
199 | [TTM147-1]HMI_ErrIface..b_Display | 75.234.313 | Download Active | A recipe download is active
200 | #N/A | 75.234.314
201 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.360 | Circuit breaker 24 V DC triggered | Breaker 24V DC manually switched OFF or triggered due to over current.
202 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.364 | No air pressure | The pressure for the air supply is not available.
203 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.367 | Waiting on air pressure feedback | Waiting on air pressure feedback at closed safety-circuit.
204 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.368 | Air suppy unit has a internal fault. | No correct air pressure feedback
205 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.370 | Restarting air suppy unit | Restarting air suppy unit after internal failure.
206 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.371 | Circuit breaker control power triggered | Breaker control power manually switched OFF or triggered due to over current.
207 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.372 | Circuit breaker main supply triggered | Breaker main supply manually switched OFF or triggered due to over current.
208 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.373 | FOR1 Circuit breaker IPD supply triggered | Breaker FOR1 IPD supply manually switched OFF or triggered due to over current.
209 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.374 | FOR1 Circuit breaker CPD supply triggered | Breaker FOR1 CPD supply manually switched OFF or triggered due to over current.
210 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.420 | LOD1 Circuit breaker IPD supply triggered | Breaker LOD1 IPD supply manually switched OFF or triggered due to over current.
211 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.424 | LOD1/INF1 Circuit breaker CPD supply triggered | Breaker LOD1/INF1 CPD supply manually switched OFF or triggered due to over current.
212 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.427 | INF2 Circuit breaker CPD supply triggered | Breaker INF2 CPD supply manually switched OFF or triggered due to over current.
213 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.428 | CLO1 Circuit breaker IPD supply triggered | Breaker CLO1 IPD supply manually switched OFF or triggered due to over current.
214 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.430 | CLO1 Circuit breaker CPD supply triggered | Breaker CLO1 CPD supply manually switched OFF or triggered due to over current.
215 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.431 | THV1 Circuit breaker IPD supply triggered | Breaker THV1 IPD supply manually switched OFF or triggered due to over current.
216 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.432 | THV1 Circuit breaker CPD supply triggered | Breaker THV1 CPD supply manually switched OFF or triggered due to over current.
217 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.433 | INF1 Circuit breaker IPD supply triggered | Breaker INF1 IPD supply manually switched OFF or triggered due to over current.
218 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.434 | INF2 Circuit breaker IPD supply triggered | Breaker INF2 IPD supply manually switched OFF or triggered due to over current.
219 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.440 | TOC1_CAB1 Circuit breaker power supply triggered | Circuit breaker TOC1_CAB1 for power supply conveyors triggered
220 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.441 | Cooling of cabinets is not effective | Cooling stream in cabinets is not effective, if any cabinet is open.
221 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.444 | Cabinets overheating | Cabinets temperature rising, because not all cabinets are closed. Cooling stream is not effective.
222 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.447 | Circuit breaker FRM1 door switch supply triggered | Breaker FRM1 door switch supply manually switched OFF or triggered due to over current.
223 | [TTM147-1]GMS_ErrIface..b_Display | 75.234.448 | LOTO switch is off | LOTO switch is off. Power is not available.
224 | #N/A | 75.234.450
225 | [TTM147-1]MIS_ErrIface..b_Display | 75.234.451 | MIS system is not ready | Check MIS system
226 | [TTM147-1]MIS_ErrIface..b_Display | 75.234.452 | MIS system is not ready | Check MIS system
| PLC2 | 75.234.453
227 | [TTM147-2]PLC2_CPU_ErrIface..b_Display | 75.234.454 | Missing Remote IO | Missing Remote IO
228 | [TTM147-2]PLC2_CPU_ErrIface..b_Display | 75.234.480 | Routine Termination Time Out | The modul wasn't able to execute the procedure in the requested time
229 | [TTM147-2]PLC2_CPU_ErrIface..b_Display | 75.234.487 | HMI Communication Error | The Communication to the HMI is not ok
230 | [TTM147-2]PLC2_CPU_ErrIface..b_Display | 75.234.488 | Task overlap occured | CPU usage is very high
231 | [TTM147-2]PLC2_CPU_ErrIface..b_Display | 75.234.490 | Task overlaps occured | CPU usage is very high
232 | #N/A | 75.234.491
233 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.492 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
234 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.493 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
235 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.494 | Too small | This is a system failure: the shown registration list is too small.
236 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.500 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
237 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.504 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
238 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.507 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
239 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.508 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
240 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.510 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
241 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.511 | Controller Timeout | Global Statemachine fault.
242 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.512 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
243 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.513 | State machine init - | This is a system failure.
244 | [TTM147-2]PLC2_SM_Ctr_ErrIface..b_Display | 75.234.514 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
| PLC3 | 75.234.580
245 | [TTM147-3]PLC3_CPU_ErrIface..b_Display | 75.234.584 | Missing Remote IO | Missing Remote IO
246 | [TTM147-3]PLC3_CPU_ErrIface..b_Display | 75.234.587 | Routine Termination Time Out | The modul wasn't able to execute the procedure in the requested time
247 | [TTM147-3]PLC3_CPU_ErrIface..b_Display | 75.234.588 | HMI Communication Error | The Communication to the HMI is not ok
248 | [TTM147-3]PLC3_CPU_ErrIface..b_Display | 75.234.590 | Task overlap occured | CPU usage is very high
249 | [TTM147-3]PLC3_CPU_ErrIface..b_Display | 75.234.591 | Task overlaps occured | CPU usage is very high
250 | #N/A | 75.234.592
251 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.593 | System init active | In the state system init all software modules were registered. At the end the plc is waiting to communicate with the HMI.
252 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.594 | System init timeout | This is a system failure: the timeout of the system initialising state elapsed because a module did not finish the initialisation. The shown module is the first module in the list whose done acknowledge is missing.
253 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.620 | Too small | This is a system failure: the shown registration list is too small.
254 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.624 | Module init error | This is a system failure: there was a double module name or a double module number detected during the registration process of the displayed module.
255 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.627 | The error list is/was full | The error list is or was full. This is the last possible entry in the error list. It generates a rapid stop for all state machines.
256 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.628 | No state acknowledge | This is a system failure: the acknowledgement for a state from a module is missing. The shown module is the first module in the list whose state acknowledge is missing.
257 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.630 | Alarm init fault | This is a system failure: there was a double error ID number or a number bigger than 3 digits. The shown module is the module with the error init fault.
258 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.631 | Power down active | The state power down is the first state after powering up the system. If there is only power for the control system this state will be active until the main power is switched on.
259 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.632 | Controller Timeout | Global Statemachine fault.
260 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.633 | Controller registration fault | This is a system failure: the controller identification is defined wrong.
261 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.634 | State machine init - | This is a system failure.
262 | [TTM147-3]PLC3_SM_Ctr_ErrIface..b_Display | 75.234.640 | Undefined error in | There is at least one undefined error. The undefined error belongs to the listed module.
INF1 |  | 75.234.641
263 | [TTM147-1]INF1_PGR1Slw_ErrIface..b_Display | 75.234.644 | Position error | Actual position has exceeded position error tolerance.
264 | [TTM147-1]INF1_PGR1Slw_ErrIface..b_Display | 75.234.647 | Clamping lever is not closed | Claming lever is open.
265 | [TTM147-1]INF1_PGR1Slw_ErrIface..b_Display | 75.234.648 | Drive fault: | Servo amplifier is in faulted state
266 | [TTM147-1]INF1_PGR1Slw_ErrIface..b_Display | 75.234.650 | Parameter setting not correct | One or more configuration parameters are not in the allowed limits or a combination of parameter values is not possible.
267 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.651 | Motion instruction error | The execution of a motion instuction failed.
268 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.652 | Homing timeout | The PGR modul wasn't able to execute the homing procedure in the requested time.
269 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.653 | Wrong number of sockets detected axis 1, detected: | Wrong numbers of sockets detected on the belt while homing the PGR.
270 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.654 | Wrong number of sockets detected axis 2, detected: | Wrong numbers of sockets detected on the belt while homing the PGR.
271 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.700 | Wrong placed sockets detected axis 1, position: | Wrong placed sockets detected on the belt while homing the PGR.
272 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.707 | Wrong placed sockets detected axis 2, position: | Wrong placed sockets detected on the belt while homing the PGR.
273 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.708 | Train didn't catch up fast enough | Train on the outfeed move didn't reach the infeed position in time.
274 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.710 | Trains to near | Train observation reports train crash.
275 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.711 | Routine stop timeout | One of the axis control routines didn't terminate properly. This is just software debug information and the machine should still work normally.
276 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.712 | Train reached warning distance | Train tries to reach an occupied outfeed position.
277 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.713 | Train reached Estop distance | Train tries to reach an occupied outfeed position.
278 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.714 | Position Cam Status lost | One or both axis have lost the position cam status.
279 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.720 | Axis gearing error | Electronic gearing of the PGR axis failed while running.
280 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.724 | Infeed crash (sensor 1) | Infeed crash mechanism reports error.
281 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.727 | Infeed crash (sensor 2) | Infeed crash mechanism reports error.
282 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.728 | PIN infeed jam | Jam sensor at PIN belt reports error.
283 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.730 | Product frequency too high | Product performance on infeed too high
284 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.731 | Acceleration for infeed step too high | Acceleration for infeed step is above the defined limits
285 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.732 | Wait for product | Wait for products from upstream
286 | [TTM147-1]INF1_PGR1Evt_ErrIface..b_Display | 75.234.733 | Topguide: Move time out | Timeout of the cylinder movement of topguide
287 | #N/A | 75.234.734
288 | [TTM147-1]INF1_UIfaceSlw_ErrIface..b_Display | 75.234.740 | Motion instruction error | Motion instruction caused error in program code
289 | [TTM147-1]INF1_UIfaceSlw_ErrIface..b_Display | 75.234.741 | Upstream machine is not homed anymore | Upstream machine lost homed state at production.
290 | [TTM147-1]INF1_UIfaceSlw_ErrIface..b_Display | 75.234.744 | Upstream machine not homed | Machine is waiting for the homed signal of the upstream maschine
291 | [TTM147-1]INF1_UIfaceSlw_ErrIface..b_Display | 75.234.747 | Upstream machine not homed in time | Upstream machine didn't home in given time.
292 | [TTM147-1]INF1_UIfaceSlw_ErrIface..b_Display | 75.234.748 | Upstream machine not deceled in time | Upstream machine didn't decelerate in given time.
293 | #N/A | 75.234.750
294 | [TTM147-1]INF1_UIfaceEvt_ErrIface..b_Display | 75.234.751 | Upstream not ready | Upstream machine is not ready. Production is not possible.
295 | [TTM147-1]INF1_UIfaceEvt_ErrIface..b_Display | 75.234.752 | CIP-Sync - data connection error | CIP-Sync connection failure to wrapper machine
296 | [TTM147-1]INF1_UIfaceEvt_ErrIface..b_Display | 75.234.753 | CIP-Sync - axis connection error | CIP-Sync connection failure to wrapper machine
297 | [TTM147-1]INF1_UIfaceEvt_ErrIface..b_Display | 75.234.754 | Standby - No products coming | HXX signalize that no products available. Switch off conveyors and vacuum pumps if possible.
298 | [TTM147-1]INF1_UIfaceEvt_ErrIface..b_Display | 75.333.001 | Check weigher not running or faulted | HCM is not allowed to produce to TTM before check weigher is running
299 | #N/A | 75.333.002
300 | [TTM147-1]INF1_DH_ErrIface..b_Display | 70.097.000 | Decel Not Finished In Time: | One or some modules at infeed finished not in time
301 | #N/A | 70.097.001
302 | [TTM147-1]INF1_HH_ErrIface..b_Display | 70.097.010 | Homing PGR not possible | PGR can not home, if loader roboter is in pick area
303 | #N/A | 70.097.011
304 | [TTM147-1]INF1_SM_ErrIface.b_StateTimeout.b_Display | 70.097.012 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
305 | [TTM147-1]INF1_SM_ErrIface.b_ServiceModeActive.b_Display | 70.097.014 | Service mode active | The machine part is in service mode.
306 | [TTM147-1]INF1_SM_ErrIface.b_CalculationActive.b_Display | 70.097.015 | Calculation active | The unit is in calculation state.
307 | [TTM147-1]INF1_SM_ErrIface.b_StateMachineDisabled.b_Display | 70.097.019 | Switched off | This machine part is disabled
308 | [TTM147-1]INF1_SM_ErrIface.b_ActivatingPwrFault.b_Display | 70.097.020 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
309 | [TTM147-1]INF1_SM_ErrIface.b_ServiceModeActive.b_Display | 70.097.021 | Clean mode active | The machine part is in clean mode.
310 | #N/A | 70.097.022
311 | [TTM147-1]INF1_PIN1Slw_ErrIface..b_Display | 70.097.024 | Drive fault: | Servo amplifier is in faulted state
312 | [TTM147-1]INF1_PIN1Slw_ErrIface..b_Display | 70.097.025 | Position error | Actual position has exceeded position error tolerance.
313 | [TTM147-1]INF1_PIN1Slw_ErrIface..b_Display | 70.097.030 | Motion error | Fault at execute motion command.
314 | [TTM147-1]INF1_PIN1Slw_ErrIface.b_PullnoseOpen.b_Display | 70.097.031 | Pullnose is open | Pullnose is open
315 | [TTM147-1]INF1_PIN1Slw_ErrIface.b_PullnoseNotClosed.b_Display | 70.097.032 | Pullnose is open | Pullnose is open
316 | #N/A | 70.097.033
317 | [TTM147-1]INF1_PBL1Fst_ErrIface.b_Display.b_Display | 70.097.034 | Validation fault | The module detected a value out of range.
318 | [TTM147-1]INF1_PBL1Fst_ErrIface.b_Display.b_Display | 70.097.040 | Blowout max. number of consecutive rejects reached | Too many consecutive rejects.
319 | [TTM147-1]INF1_PBL1Fst_ErrIface.b_Display.b_Display | 70.097.041 | Reject sensor fault | Sensor always covered
320 | [TTM147-1]INF1_PBL1Fst_ErrIface.b_Display.b_Display | 70.097.050 | Jam before or detection fault on step-sensor | Sensor do not detect products. Maybe products jams before sensor or detection do not correct.
321 | [TTM147-1]INF1_PBL1Fst_ErrIface..b_Display | 70.097.051 | Motion instruction error | Internal fault at execute motion command.
INF2 |  | 70.097.052
322 | [TTM147-1]INF2_PGR1Slw_ErrIface..b_Display | 70.097.053 | Position error | Actual position has exceeded position error tolerance.
323 | [TTM147-1]INF2_PGR1Slw_ErrIface..b_Display | 70.097.054 | Clamping lever is not closed | Claming lever is open.
324 | [TTM147-1]INF2_PGR1Slw_ErrIface..b_Display | 70.097.060 | Drive fault: | Servo amplifier is in faulted state
325 | [TTM147-1]INF2_PGR1Slw_ErrIface..b_Display | 70.097.061 | Parameter setting not correct | One or more configuration parameters are not in the allowed limits or a combination of parameter values is not possible.
326 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.062 | Motion instruction error | The execution of a motion instuction failed.
327 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.063 | Homing timeout | The PGR modul wasn't able to execute the homing procedure in the requested time.
328 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.064 | Wrong number of sockets detected axis 1, detected: | Wrong numbers of sockets detected on the belt while homing the PGR.
329 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.065 | Wrong number of sockets detected axis 2, detected: | Wrong numbers of sockets detected on the belt while homing the PGR.
330 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.070 | Wrong placed sockets detected axis 1, position: | Wrong placed sockets detected on the belt while homing the PGR.
331 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.071 | Wrong placed sockets detected axis 2, position: | Wrong placed sockets detected on the belt while homing the PGR.
332 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.072 | Train didn't catch up fast enough | Train on the outfeed move didn't reach the infeed position in time.
333 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.073 | Trains to near | Train observation reports train crash.
334 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 70.097.104 | Routine stop timeout | One of the axis control routines didn't terminate properly. This is just software debug information and the machine should still work normally.
335 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.000 | Train reached warning distance | Train tries to reach an occupied outfeed position.
336 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.001 | Train reached Estop distance | Train tries to reach an occupied outfeed position.
337 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.002 | Position Cam Status lost | One or both axis have lost the position cam status.
338 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.003 | Axis gearing error | Electronic gearing of the PGR axis failed while running.
339 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.004 | Infeed crash (sensor 1) | Infeed crash mechanism reports error.
340 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.010 | Infeed crash (sensor 2) | Infeed crash mechanism reports error.
341 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.011 | PIN infeed jam | Jam sensor at PIN belt reports error.
342 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.012 | Product frequency too high | Product performance on infeed too high
343 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.013 | Acceleration for infeed step too high | Acceleration for infeed step is above the defined limits
344 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.040 | Wait for product | Wait for products from upstream
345 | [TTM147-1]INF2_PGR1Evt_ErrIface..b_Display | 76.140.041 | Topguide: Move time out | Timeout of the cylinder movement of topguide
346 | #N/A | 76.140.042
347 | [TTM147-1]INF2_UIfaceSlw_ErrIface..b_Display | 76.140.043 | Motion instruction error | Motion instruction caused error in program code
348 | [TTM147-1]INF2_UIfaceSlw_ErrIface..b_Display | 76.140.044 | Upstream machine is not homed anymore | Upstream machine lost homed state at production.
349 | [TTM147-1]INF2_UIfaceSlw_ErrIface..b_Display | 76.140.045 | Upstream machine not homed | Machine is waiting for the homed signal of the upstream maschine
350 | [TTM147-1]INF2_UIfaceSlw_ErrIface..b_Display | 76.140.046 | Upstream machine not homed in time | Upstream machine didn't home in given time.
351 | [TTM147-1]INF2_UIfaceSlw_ErrIface..b_Display | 76.140.061 | Upstream machine not deceled in time | Upstream machine didn't decelerate in given time.
352 | #N/A | 76.140.062
353 | [TTM147-1]INF2_UIfaceEvt_ErrIface..b_Display | 76.140.064 | Upstream not ready | Upstream machine is not ready. Production is not possible.
354 | [TTM147-1]INF2_UIfaceEvt_ErrIface..b_Display | 76.140.065 | CIP-Sync - data connection error | CIP-Sync connection failure to wrapper machine
355 | [TTM147-1]INF2_UIfaceEvt_ErrIface..b_Display | 76.140.066 | CIP-Sync - axis connection error | CIP-Sync connection failure to wrapper machine
356 | [TTM147-1]INF2_UIfaceEvt_ErrIface..b_Display | 76.140.070 | Standby - No products coming | HXX signalize that no products available. Switch off conveyors and vacuum pumps if possible.
357 | [TTM147-1]INF2_UIfaceEvt_ErrIface..b_Display | 76.140.071 | Check weigher not running or faulted | HCM is not allowed to produce to TTM before check weigher is running
358 | #N/A | 76.140.072
359 | [TTM147-1]INF2_DH_ErrIface..b_Display | 76.140.081 | Decel Not Finished In Time: | One or some modules at infeed finished not in time
360 | #N/A | 76.140.082
361 | [TTM147-1]INF2_HH_ErrIface..b_Display | 76.140.083 | Homing PGR not possible | PGR can not home, if loader roboter is in pick area
362 | #N/A | 76.140.084
363 | [TTM147-1]INF2_SM_ErrIface.b_StateTimeout.b_Display | 76.140.085 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
364 | [TTM147-1]INF2_SM_ErrIface.b_ServiceModeActive.b_Display | 76.140.086 | Service mode active | The machine part is in service mode.
365 | [TTM147-1]INF2_SM_ErrIface.b_CalculationActive.b_Display | 76.140.087 | Calculation active | The unit is in calculation state.
366 | [TTM147-1]INF2_SM_ErrIface.b_StateMachineDisabled.b_Display | 76.140.087 | Switched off | This machine part is disabled
367 | [TTM147-1]INF2_SM_ErrIface.b_ActivatingPwrFault.b_Display | 76.140.090 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
368 | [TTM147-1]INF2_SM_ErrIface.b_ServiceModeActive.b_Display | 76.140.091 | Clean mode active | The machine part is in clean mode.
369 | #N/A | 76.140.092
370 | [TTM147-1]INF2_PIN1Slw_ErrIface..b_Display | 76.140.093 | Drive fault: | Servo amplifier is in faulted state
371 | [TTM147-1]INF2_PIN1Slw_ErrIface..b_Display | 76.140.106 | Position error | Actual position has exceeded position error tolerance.
372 | [TTM147-1]INF2_PIN1Slw_ErrIface..b_Display | 76.140.121 | Motion error | Fault at execute motion command.
373 | [TTM147-1]INF2_PIN1Slw_ErrIface.b_PullnoseOpen.b_Display | 76.140.122 | Pullnose is open | Pullnose is open
374 | [TTM147-1]INF2_PIN1Slw_ErrIface.b_PullnoseNotClosed.b_Display | 76.140.126 | Pullnose is open | Pullnose is open
375 | #N/A | 76.140.127
376 | [TTM147-1]INF2_PBL1Fst_ErrIface.b_Display.b_Display | 76.140.130 | Validation fault | The module detected a value out of range.
377 | [TTM147-1]INF2_PBL1Fst_ErrIface.b_Display.b_Display | 76.140.160 | Blowout max. number of consecutive rejects reached | Too many consecutive rejects.
378 | [TTM147-1]INF2_PBL1Fst_ErrIface.b_Display.b_Display | 76.140.162 | Reject sensor fault | Sensor always covered
379 | [TTM147-1]INF2_PBL1Fst_ErrIface.b_Display.b_Display | 76.140.163 | Jam before or detection fault on step-sensor | Sensor do not detect products. Maybe products jams before sensor or detection do not correct.
380 | [TTM147-1]INF2_PBL1Fst_ErrIface..b_Display | 76.140.164 | Motion instruction error | Internal fault at execute motion command.
LOD1 |  | 76.140.165
381 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.166 | Actual position Tool Center Point (TCP) out of range | The actual position of the Tool Center Point (TCP) is outside of the allowed working range
382 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.168 | Command position Tool Center Point (TCP) out of range | The command position of the Tool Center Point (TCP) is outside of the allowed working range
383 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.170 | Actual position Tool Center Point (TCP) out of range | The actual position of the Tool Center Point (TCP) is outside of the allowed working range
384 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.171 | Excessive error on Tool Center Point (TCP) | The allowed difference between two program scans to large.
385 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.172 | Actual position Joint 4 (P4) out of range | The actual position of Joint 4 (P4) is outside of the allowed working range
386 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.181 | Command position Joint 4 (P4) out of range | The command position of Joint 4 (P4) is outside of the allowed working range
387 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.182 | Actual position Joint 4 (P4) out of range | The actual position of Joint 4 (P4) is outside of the allowed working range
388 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.183 | Excessive error on position Joint 4 (P4) | The allowed difference between two program scans to large.
389 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.184 | Excessive error on Joint 2 | The allowed difference between two program scans to large.
390 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.190 | Excessive error on Joint 3 | The allowed difference between two program scans to large.
391 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.191 | Excessive error on Joint 4 | The allowed difference between two program scans to large.
392 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.192 | Absolute position Error | A position which has to be absolute is defined as relative position
393 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.201 | Relative position Error | No absolute reference position is defined for relative positions
394 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.202 | Repos of robot required | Repositioning of Robot required
395 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.210 | Absolute position not in working area : | An absolute position is outside the defined working area
396 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.211 | Working area error | The working area of P4 is bigger than the frame size
397 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.212 | Motion Instruction Error | Motion Instruction Error in the software
398 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.213 | Routine stop timeout | Routine Stop Timeout in the software
399 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.221 | Routine termination timeout | Routine Termination Timeout in the software
400 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.222 | Joint 2 torque to hight : | Torque higher than allowed limit for the gear box
401 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.223 | Joint 3 torque to hight : | Torque higher than allowed limit for the gear box
402 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.224 | Joint 4 torque to hight : | Torque higher than allowed limit for the gear box
403 | [TTM147-1]LOD1_RBT1Evt_ErrIface..b_Display | 76.140.225 | Neighbouring robot out of range | Neighbouring robot is out of the defined working range and this raises the risc of a collision
404 | #N/A | 76.140.226
405 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 76.140.227 | Motion Instruction Error | Motion Instruction Error in the software
406 | #N/A | 76.140.228
407 | [TTM147-1]LOD1_VAC1_ErrIface..b_Display | 76.140.229 | Vacuum Pump OFF | Vacuum pump is turned off
408 | #N/A | 76.140.230
409 | [TTM147-1]LOD1_SM_ErrIface.b_StateTimeout.b_Display | 76.140.231 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
410 | [TTM147-1]LOD1_SM_ErrIface.b_ServiceModeActive.b_Display | 76.140.232 | Service mode active | The machine part is in service mode.
411 | [TTM147-1]LOD1_SM_ErrIface.b_CalculationActive.b_Display | 76.140.260 | Calculation active | The unit is in calculation state.
412 | [TTM147-1]LOD1_SM_ErrIface.b_StateMachineDisabled.b_Display | 76.140.261 | Switched off | This machine part is disabled
413 | [TTM147-1]LOD1_SM_ErrIface.b_ActivatingPwrFault.b_Display | 76.140.262 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
414 | #N/A | 79.390.000
415 | [TTM147-1]LOD1_DH_ErrIface..b_Display | 79.390.001 | Decel Not Finished In Time: | The Decelhandler wasn't able to finish in the requested time
416 | #N/A | 79.390.002
417 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.390.003 | Gripper crashed | Description : The Gripper collided with something
418 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.390.004 | Grouping fingers failed | Description : The gripper fingers grouping function is too slow
419 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.390.005 | Ungrouping fingers failed | Description : The gripper fingers ungrouping function is too slow
420 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.390.006 | Gripper not connected | Description : No gripper installed or gripper not locked
421 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.391.001 | Wrong gripper installed | Description : Disagreement between the input gripper code and the gripper code from the recipe parameters
422 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.391.002 | Gripper network fault | Description : The gripper network is interrupted.
423 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.391.003 | Ejector move failed | Description : The ejector movement is too slow or does not reach the end position
424 | [TTM147-1]LOD1_GRL1_ErrIface..b_Display | 79.392.000 | Batch miscount sensor function failure | Description : After the drop of the products should not recognize the gripper products
425 | #N/A | 79.392.001
426 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.392.003 | Drive Fault Axis 2: | The drive of axis 2 is in fault state
427 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.393.000 | Axis 2 not enabled | Axis 2 not enabled
428 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.393.001 | Axis 2 not Calibrated | Axis 2 is not calibrated
429 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.393.003 | Limit Warning Axis 2 | Axis 2 has excessed a software or hardware limit
430 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.580.001 | Software Limit Fault Axis 2 | Axis 2 has excessed a software limit
431 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.580.002 | Hardware Limit Fault Axis 2 | Axis 2 has excessed a hardware limit
432 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.580.003 | Axis 2 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
433 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.580.004 | Brake released Axis 2 | The mechanical brake of axis 2 was released manually
434 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.580.100 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
435 | #N/A | 79.580.101
436 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.001 | Drive Fault Axis 3: | The drive of axis 3 is in fault state
437 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.002 | Axis 3 not enabled | Axis 3 not enabled
438 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.003 | Axis 3 not Calibrated | Axis 3 is not calibrated
439 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.004 | Limit Warning Axis 3 | Axis 3 has excessed a software or hardware limit
440 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.005 | Software Limit Fault Axis 3 | Axis 3 has excessed a software limit
441 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.006 | Hardware Limit Fault Axis 3 | Axis 3 has excessed a hardware limit
442 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.007 | Axis 3 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
443 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.008 | Brake released Axis 3 | The mechanical brake of axis 3 was released manually
444 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.583.100 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
445 | #N/A | 79.583.101
446 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.591.000 | Drive Fault Axis 4: | The drive of axis 4 is in fault state
447 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.591.001 | Axis 4 not enabled | Axis 4 not enabled
448 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.591.003 | Axis 4 not Calibrated | Axis 4 is not calibrated
449 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.591.007 | Limit Warning Axis 4 | Axis 4 has excessed a software or hardware limit
450 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.591.100 | Software Limit Fault Axis 4 | Axis 4 has excessed a software limit
451 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 79.591.102 | Hardware Limit Fault Axis 4 | Axis 4 has excessed a hardware limit
452 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 77.234.000 | Axis 4 brake test at power off not passed | At each axle switch-off cycle (axle no longer regulated), a brake test is performed, which checks the axle position before and after. If the motor has moved by a few degrees, this error is triggered. Therefore the safety doors are also locked until the error message is reset or an emergency stop safety circuit was opened.
453 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 77.234.000 | Brake released Axis 4 | The mechanical brake of axis 4 was released manually
454 | [TTM147-1]LOD1_RBT1Slw_ErrIface..b_Display | 77.234.000 | Failed to change axis-brake settings | Axis-Brake settings could not changed.
MCTR |  | 77.234.000
455 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Hardware not ok! | Description:\nThe monitoring of the safety circuit shows an error. There is either a problem with the emergency stop button circuit or with the door safety circuit. This is a serious problem and has to be solved!\n\n
456 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Software disagreement with Hardware channels | Description:\n Hardware Channel Signals are not correct with E-Stop State
457 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Reset required | It is required to press the reset button to reset the safety circuit relay
458 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop cabinet | Description: The emergency stop button at the machine is pressed.\n
459 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop HMI | Description: The emergency stop button at the machine is pressed.\n
460 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop FOR1 | Description: The emergency stop button at the machine is pressed.\n
461 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop LOD1 | Description: The emergency stop button at the machine is pressed.\n
462 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop CLO1 Front | Description: The emergency stop button at the machine is pressed.\n
463 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop CLO1 Rear | Description: The emergency stop button at the machine is pressed.\n
464 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop FOC1 Rear | Description: The emergency stop button at the machine is pressed.\n
465 | [TTM147-1]TTM_Saf1_ErrIface..b_Display | 77.234.000 | Emergency stop LID1 | Description: The emergency stop button at the machine is pressed.\n
466 | #N/A | 77.234.000
467 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | SD-Module: No Ethernet Connection | Description: Faulty ethernet connection between SPS and SD Module.
468 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | SD-Module: Gateway interface error | Description: SD Gateway Interface centralized alarm.Invalid SD data.
469 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | SD-Module: Initialisation error | Description: SD bus initialisation error. Possibly no SD slave connected!
470 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | SD-Module: Teach error | Description: Count of detected doors is not correct.
471 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | SD-Module: Short circuit on Gateway interface | Description: Short-circuit in the SD interface wires
472 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | SD-Module: Communication error to doors | Description: One or more SD slaves unavailable. Invalid data from the SD slaves.
473 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | SD-Module: Internal error of one or more doors | Description: One or more SD slaves have a internal error.
474 | #N/A | 77.234.000
475 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 1 open | Description : Somebody or something opened the door
476 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 2 open | Description : Somebody or something opened the door
477 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 3 open | Description : Somebody or something opened the door
478 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 4 open | Description : Somebody or something opened the door
479 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 5 open | Description : Somebody or something opened the door
480 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 6 open | Description : Somebody or something opened the door
481 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 7 open | Description : Somebody or something opened the door
482 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 8 open | Description : Somebody or something opened the door
483 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 9 open | Description : Somebody or something opened the door
484 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 10 open | Description : Somebody or something opened the door
485 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 11 open | Description : Somebody or something opened the door
486 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 12 open | Description : Somebody or something opened the door
487 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 13 open | Description : Somebody or something opened the door
488 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 14 open | Description : Somebody or something opened the door
489 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 15 open | Description : Somebody or something opened the door
490 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 16 open | Description : Somebody or something opened the door
491 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 17 open | Description : Somebody or something opened the door
492 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 18 open | Description : Somebody or something opened the door
493 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 19 open | Description : Somebody or something opened the door
494 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 20 open | Description : Somebody or something opened the door
495 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Cover open (blank size plate) | Description : Somebody or something opened the cover
496 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Cover open (blank size plate) | Description : Somebody or something opened the cover
497 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Cover open (blank size plate) | Description : Somebody or something opened the cover
498 | #N/A | 77.234.000
499 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 1 not locked | Description : door is not locked any more
500 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 2 not locked | Description : door is not locked any more
501 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 3 not locked | Description : door is not locked any more
502 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 4 not locked | Description : door is not locked any more
503 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 5 not locked | Description : door is not locked any more
504 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 6 not locked | Description : door is not locked any more
505 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 7 not locked | Description : door is not locked any more
506 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 8 not locked | Description : door is not locked any more
507 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 9 not locked | Description : door is not locked any more
508 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 10 not locked | Description : door is not locked any more
509 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 11 not locked | Description : door is not locked any more
510 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 12 not locked | Description : door is not locked any more
511 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 13 not locked | Description : door is not locked any more
512 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 14 not locked | Description : door is not locked any more
513 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 15 not locked | Description : door is not locked any more
514 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 16 not locked | Description : door is not locked any more
515 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 17 not locked | Description : door is not locked any more
516 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 18 not locked | Description : door is not locked any more
517 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 19 not locked | Description : door is not locked any more
518 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door 20 not locked | Description : door is not locked any more
519 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Doors mapping not done | Description : door is not mapped with the node idx of SD-Bus
520 | #N/A | 77.234.000
521 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door zone reset LOD1 needed | Door of zone LOD1 was opened. Reset of this zone needed.
522 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door zone reset GEN1 needed | Door of zone GEN1 was opened. Reset of this zone needed.
523 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door zone reset FOR1 needed | Door of zone FOR1 was opened. Reset of this zone needed.
524 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door zone reset CLO1 needed | Door of zone CLO1 was opened. Reset of this zone needed.
525 | [TTM147-1]TTM_Saf2_ErrIface..b_Display | 77.234.000 | Door zone reset LID1 needed | Door of zone LID1 was opened. Reset of this zone needed.
526 | #N/A | 77.234.000
527 | [TTM147-1]TTM_SH_ErrIface..b_Display | 77.234.000 | Statemachine Handler disabled | Statemachine Handler is disabled, statemachines of this machine controller are independet
528 | [TTM147-1]TTM_SH_ErrIface..b_Display | 77.234.000 | Glue units set to low temperature | Glue units are set to low temperature mode
529 | #N/A | 77.234.000
530 | [TTM147-1]TTM_DH_ErrIface..b_Display | 77.234.000 | Global Decel handler disabled | Global Decel Handler is disabled, statemachines of this machine controller can stopp independet
531 | #N/A | 77.234.000
532 | [TTM147-1]TTM_SMCtr_ErrIface..b_Display | 77.234.000 | Empty mode active | The machine is in empty mode
533 | [TTM147-1]TTM_SMCtr_ErrIface..b_Display | 77.234.000 | Condition Timeout | A Stop, Reset or Start Button is blocked or has a wire break
THV |  | 77.234.000
534 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Parameter Setting not correct | One or more configuration parameters are not in the allowed limits or a combination of parameter values is not possible
535 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Axis Position Error | Actual position has exceeded position error tolerance
536 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Axis Drive Fault | Servo amplifier is in faulted state
537 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Axis Validation Fault
538 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Home Registration Sensor Fault | No signal from the home switch during calibration process
539 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Axis not Calibrated | One ore more of the axis have lost the absolut position
540 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Test Position Error | In the test mode, the distance of two carriers is less then the minimum distance
541 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | TrayClamping SensorError on the Former | The sensor of the clamping cylinder on the former has the end position not detected
542 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | TrayClamping SensorError on the Closer | The sensor of the clamping cylinder on the closer has the end position not detected
543 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | To few Carrier in system | During the home routine wasn't enough carriers detected
544 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | To many Carrier in the system | During the home routine was too many carriers detected
545 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Former robot is in Working Area | The roboter of the former module is in the working area of the tray transport
546 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Loader robot is in Working Area | The roboter of the loader module is in the working area of the tray transport
547 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Closer robot is in Working Area | The roboter of the closer module is in the working area of the tray transport
548 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Former Tray Clamping is not closed | The clamping of the trays on the former module is not closed and the tray transport can not moving
549 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Closer Tray Clamping is not closed | The clamping of the trays on the closer module is not closed and the tray transport can not moving
550 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Wait for Robot out of working area | Wait till all roboter are out of the working area
551 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Carrier not synched | Carrier are noch synched
552 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Home Registration Sensor Inconsistence | The number of carriers counted by the registration sensor (belt 4) doesn't correspond to the number counted by the control sensor (belt 6)
553 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Home Carrier Distance Error | The distance between the carriers does not correspond to the parametrized value.
554 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Homing blocked | All transitions are blocked, it is not possible to finish the homing routine.
555 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Motion Instruction Error | The execution of a motion instruction wasn't sucessful
556 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Routine stop timeout | Routine Stop Timeout in the software
557 | [TTM147-2]THV1_VTT1Cnt_ErrIface..b_Display | 77.234.000 | Routine termination timeout | The modul wasn't able to execute the procedure in the requested time
558 | #N/A | 77.234.000
559 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 00 Drive Fault | Servo amplifier is in faulted state
560 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 02 Drive Fault | Servo amplifier is in faulted state
561 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 04 Drive Fault | Servo amplifier is in faulted state
562 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 05 Drive Fault | Servo amplifier is in faulted state
563 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 06 Drive Fault | Servo amplifier is in faulted state
564 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 07 Drive Fault | Servo amplifier is in faulted state
565 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 08 Drive Fault | Servo amplifier is in faulted state
566 | [TTM147-2]THV1_VTTCnt_ErrIface..b_Display | 77.234.000 | Axis 10 Drive Fault | Servo amplifier is in faulted state
567 | #N/A | 77.234.000
568 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Position Error on Belt 0 | The position of one ore more carriers is not correct
569 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Position Error on Belt 2 | The position of one ore more carriers is not correct
570 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Position Error on Belt 4 | The position of one ore more carriers is not correct
571 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Position Error on Belt 6 | The position of one ore more carriers is not correct
572 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Position Error on Belt 8 | The position of one ore more carriers is not correct
573 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Position Error on Belt 10 | The position of one ore more carriers is not correct
574 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Number Error on Belt 0 | The number of detected carriers is not correct
575 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Number Error on Belt 2 | The number of detected carriers is not correct
576 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Number Error on Belt 4 | The number of detected carriers is not correct
577 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Number Error on Belt 6 | The number of detected carriers is not correct
578 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Number Error on Belt 8 | The number of detected carriers is not correct
579 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Carrier Number Error on Belt 10 | The number of detected carriers is not correct
580 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Tray Number Error | The tray detection sensor on belt 6 detects no trays
581 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Tray Clamping Error on Former | The sensor of the clamping cylinder on the former has the end position not in the requested time detected
582 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Tray Clamping Error on Closer | The sensor of the clamping cylinder on the closer has the end position not in the requested time detected
583 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Empty Mode Done | The Empty Mode has fininshed and stopped the machine
584 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Tray Closing no more possible | The Closing of the trays is not possible
585 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Box on Carrier after Closer | Box on carrier detected after closer robot
586 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Consecutive miscount | Consecutive product miscount detected
587 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Consecutive miscount sensor allways covered fault | Consecutive miscount sensor allways covered detected
588 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Motion Instruction Error | The execution of a motion instruction wasn't sucessful
589 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Routine stop timeout | Routine Stop Timeout in the software
590 | [TTM147-2]THV1_VTT1Evt_ErrIface..b_Display | 77.234.000 | Routine termination timeout | The modul wasn't able to execute the procedure in the requested time
591 | #N/A | 77.234.000
592 | [TTM147-2]THV1_DH_ErrIface..b_Display | 77.234.000 | Deceleration not finished in time: | The modul wasn't able to stop correctly the procedure in the requested time
593 | #N/A | 77.234.000
594 | [TTM147-2]THV1_SM_ErrIface..b_Display | 77.234.000 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
595 | [TTM147-2]THV1_SM_ErrIface..b_Display | 77.234.000 | Service mode active | The machine part is in service mode.
596 | [TTM147-2]THV1_SM_ErrIface..b_Display | 77.234.000 | Calculation active | The unit is in calculation state.
597 | [TTM147-2]THV1_SM_ErrIface..b_Display | 77.234.000 | Switched off | This machine part is disabled
598 | [TTM147-2]THV1_SM_ErrIface..b_Display | 77.234.000 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
TOC1 |  | 77.234.000
599 | [TTM147-3]TOC1_DH_ErrIface..b_Display | 1 | Deceleration not finished in time: | The modul wasn't able to stop correctly the procedure in the requested time
600 |  | 1
601 | [TTM147-3]TOC1_SM_ErrIface.b_StateTimeout.b_Display | 1 | State timeout | This is a system failure of this unit. There was a timeout in a state need to change to another state within a defined time. The shown module is the first module in the list whose done acknowledge is missing.
602 | [TTM147-3]TOC1_SM_ErrIface.b_ServiceModeActive.b_Display | 1 | Service mode active | The machine part is in service mode.
603 | [TTM147-3]TOC1_SM_ErrIface.b_CalculationActive.b_Display | 1 | Calculation active | The unit is in calculation state.
604 | [TTM147-3]TOC1_SM_ErrIface.b_StateMachineDisabled.b_Display | 1 | Switched off | This machine part is disabled
605 | [TTM147-3]TOC1_SM_ErrIface.b_ActivatingPwrFault.b_Display | 1 | Activating power timeout | There was a timeout while activating the drives. The shown module is the first module in the list whose done acknowledge is missing.
606 | [TTM147-3]TOC1_SM_ErrIface.b_ServiceModeActive.b_Display | 1 | Clean mode active | The machine part is in clean mode.
607 |  | 1
608 | [TTM147-3]TOC1_DSC1Med_ErrIface..b_Display | 1 | Motion Instruction Error | The execution of a motion instuction failed.
609 | [TTM147-3]TOC1_DSC1Med_ErrIface..b_Display | 1 | Routine Stop Timeout | Control routines didn't terminate properly.
610 | [TTM147-3]TOC1_DSC1Med_ErrIface..b_Display | 1 | Routine Termination Timeout | Routine termination timeout.
611 | [TTM147-3]TOC1_DSC1Med_ErrIface..b_Display | 1 | Offline calculation not successfully | The offline calculation wasn't completed successfully
612 |  | 1
613 | [TTM147-3]TOC1_DSC1Slw_ErrIface..b_Display | 1 | Drive Fault Axis | The drive of axis is in fault state.
614 | [TTM147-3]TOC1_DSC1Slw_ErrIface..b_Display | 1 | Overtemperature motor | Motor temperature sensor detects an overtemperature
615 | [TTM147-3]TOC1_DSC1Slw_ErrIface..b_Display | 1 | Overtemperature drive | Drive detects an overtemperature
616 | [TTM147-3]TOC1_DSC1Slw_ErrIface..b_Display | 1 | Disconnector off | Diconnector swiched off
617 | [TTM147-3]TOC1_DSC1Slw_ErrIface..b_Display | 1 | Aborted drive not ready | Aborted because drive not ready
618 | [TTM147-3]TOC1_DSC1Slw_ErrIface..b_Display | 1 | Motion Instruction Error | The execution of a motion instuction failed.
619 | [TTM147-3]TOC1_DSC1Slw_ErrIface..b_Display | 1 | Routine Stop Timeout | Control routines didn't terminate properly.
620 |  | 1
621 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Drive Fault Axis | The drive of axis is in fault state.
622 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Overtemperature motor | Motor temperature sensor detects an overtemperature
623 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Overtemperature drive | Drive detects an overtemperature
624 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Disconnector off | Diconnector swiched off
625 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Aborted drive not ready | Aborted because drive not ready
626 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Motion Instruction Error | The execution of a motion instuction failed.
627 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Routine Stop Timeout | Control routines didn't terminate properly.
628 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Routine Termination Timeout | Routine termination timeout.
629 | [TTM147-3]TOC1_DSC2_ErrIface..b_Display | 1 | Offline calculation not successfully | The offline calculation wasn't completed successfully
630 |  | 1
631 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Flap-Sensor S1 IO-Link fault | Communication between IO-Link Master u. Sensor has a fault.
632 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Flap-Sensor F1 IO-Link fault | Communication between IO-Link Master u. Sensor has a fault.
633 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Sideflap sensor detection fault | Flap sensor has not detected tray. Check parameter for switch distance of sensor .
634 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Frontflap sensor test failed | Front flap sensor did not detect flaps. Glue station not glues front flap of first tray to check function.
635 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Consecutive batch reject | Due to missing, shifted or jammed trays, several batches have been rejected. Those trays didn't arrive in the expected alignment. The maximum allowed number of faulty batches to pass this situation can be configured.
636 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Consecutive tray outside expectation range | Several trays have been detected outside the expected working range in a row.
637 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Consecutive open flaps | Several trays have been detected with open flaps in a row.
638 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Routine Termination Timeout | Routine termination timeout.
639 | [TTM147-3]TOC1_TFD1_ErrIface..b_Display | 1 | Offline calculation not successfully | The offline calculation wasn't completed successfully
640 |  | 1
641 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Sensor covered during startup move | It is checked at startup if a tray between the trigger and verification sensor is present.
642 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Tray to long | Trigger sensor has detected an excessively long box
643 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Tray to tray distance to short | Trigger sensor has a too small tray gap detected
644 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Tray not rejected in time | Reject sensor has not detected the rejected tray in a certain time
645 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Jam at rejection senor | Reject sensor detects a jam at reject station
646 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Not rejected tray at verification sensor | Verification sensor has detected a not rejected tray
647 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Verification sensor fault | Verification sensor doesn't detect trays, which are recognised at trigger sensor and passed the reject station
648 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Reject station disabled | Disable button of rejetion pressed.
649 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Consecutive batch reject | Due to missing, shifted or jammed trays, several batches have been rejected. Those trays didn't arrive in the expected alignment. The maximum allowed number of faulty batches to pass this situation can be configured.
650 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Consecutive tray outside expectation range | Several trays have been detected outside the expected working range in a row.
651 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Routine Termination Timeout | Routine termination timeout.
652 | [TTM147-3]TOC1_TRS1_ErrIface..b_Display | 1 | Offline calculation not successfully | The offline calculation wasn't completed successfully
653 |  | 1
654 | [TTM147-3]TOC1_DIface_ErrIface..b_Display | 1 | Downstream not ready | There is no ready signal of the downstream machine
655 | [TTM147-3]TOC1_DIface_ErrIface..b_Display | 1 | Jam on Outfeed | Outfeed sensor is covered
656 | [TTM147-3]TOC1_DIface_ErrIface..b_Display | 1 | Printer not ready | Printer not ready - Downstream blocked
657 |  | 1
658 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Databuffer full | The tray status information buffer reached the maximum number of entrys
659 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Invalid parameter | One or more parameters contains invalid values.
660 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Invalid belt configuration | The configured unwind of a DSC belt axis is too small or the belt length too big
661 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Array size too small | The defined array sizes are too small
662 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Data inconsistent | The internal consistency check detected invalid conditions
663 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Timeout station | A station didn't answering in a defined time.
664 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Missing response station | A station didn't answering before the following tray has arrived in the working area.
665 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Working area overlap station | The configured working area is too big. There are more than one tray in this area.
666 | [TTM147-3]TOC1_DTR1_ErrIface..b_Display | 1 | Routine Termination Timeout | Routine termination timeout.
PLC 1 Data
Data# | Processor Tag |  | Value | Concentrator Tag | Path IP | Description | Python Variable Name
1 | [TTM147]TTM_b_running |  | 1 | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.40 | Machine Running
2 | [TTM147]TTM_b_ready |  | 1 | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].1 | 10.168.100.40 | Machine Ready (Stopped)
3 | [TTM147]TTM_b_waiting |  | 1 | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].2 | 10.168.100.40 | Machine Ready (Waiting)
4 | [TTM147]TTM_b_alarm |  | 1 | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].3 | 10.168.100.40 | Alarm Present
5 | [TTM147]HMI_Cmd.BtnEnShift1.b_Active |  | 1 | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].11 | 10.168.100.40 | Shift 1 Enabled
6 | [TTM147]HMI_Cmd.BtnEnShift2.b_Active |  | 1 | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].12 | 10.168.100.40 | Shift 2 Enabled
7 | [TTM147]HMI_Cmd.BtnEnShift3.b_Active |  | 1 | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].13 | 10.168.100.40 | Shift 3 Enabled
| [TTM147]UIFACE1_OUT.b_Ready |  |  | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].14 | 10.168.100.40 | Infeed 1 ready
| [TTM147]UIFAC22_OUT.b_Ready |  |  | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[0].15 | 10.168.100.40 | Infeed 2 Ready
8 | [TTM147]STA_Hmi.PresentShift.Performance_Mc.dn_ProdIn |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.40 | Wrapped Packs In | ttm_147_wrapped_packs_in
9 | [TTM147]STA_Hmi.PresentShift.Performance_Mc.dn_TraysOut |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[11] | 10.168.100.40 | Cartons Out | ttm_147_cartons_out
10 | [TTM147]STA_Hmi.PresentShift.Performance_INF1.dn_ProdIn |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.40 | Wrapped Packs from Infeed 1 | ttm_147_wrapped_packs_from_infeed_1
11 | [TTM147]STA_Hmi.PresentShift.Performance_INF2.dn_ProdIn |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[13] | 10.168.100.40 | Wrapped Packs from Infeed 2 | ttm_147_wrapped_packs_from_infeed_2
12 | [TTM147]STA_Hmi.PresentShift.Misc_MC.dn_FaultStops |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[14] | 10.168.100.40 | Number of Faults | ttm_147_number_of_fault_stops_this_shift
13 | [TTM147]STA_Hmi.LasttShift.Misc_MC.dn_FaultStops |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[15] | 10.168.100.40 | Number of fault stops last shift
14 | [TTM147]STA_Hmi.PresentShift.Misc_MC.dn_FaultStops |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[16] | 10.168.100.40 | Number of fault stops prev shift
15 | [TTM147]STA_Hmi.PresentShift.OEE.r_OEE |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Process_Values[10] | 10.168.100.40 | OEE | ttm_147_oee
16 | [TTM147]STA_Hmi.PresentShift.OEE.r_Availability |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Process_Values[11] | 10.168.100.40 | Availability | ttm_147_availability
17 | [TTM147]STA_Hmi.CurCounter.r_CurProductsPerMinuteAtINF1 |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Process_Values[12] | 10.168.100.40 | ppm Sig 1 | ttm_147_ppm_inf1
18 | [TTM147]STA_Hmi.CurCounter.r_CurProductsPerMinuteAtINF2 |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Process_Values[13] | 10.168.100.40 | ppm Sig 2 | ttm_147_ppm_inf2
19 | [TTM147]STA_Hmi.PresentShift.Performance_Mc.r_TraysPerMinute |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Process_Values[14] | 10.168.100.40 | trays/min discharge | ttm_147_trays_min_discharge
20
|  |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.40
|  |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.40
|  |  | Var |  | 10.168.100.40
12 | [TTM147]FXX1_SVProd3D_Hmi.Counter.dn_ProdOut |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.40 | Product count ater 3D Profile
13 | [TTM147]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooLong |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.40 | Rejected Count for Too Long
14 | [TTM147]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooHigh |  | Var | ComData_TTM_147_1_Alpha_To_Skynet.Status_Bits[12] | 10.168.100.40 | Rejected Count for Too High
15 | [TTM147]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooWide |  | Var | ComData_TTM_147_Alpha_To_Skynet.Status_Bits[18] | 10.168.100.40 | Rejected Count for Too Wide
16 | [TTM147]HXX_InfRej_Hmi.counter.dn_ProdWaste |  | Var | ComData_TTM_147_Alpha_To_Skynet.Status_Bits[19] | 10.168.100.40 | Rows Distributed into Buffer
17 | [TTM147]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooShort |  | Var | ComData_TTM_147_Alpha_To_Skynet.Status_Bits[20] | 10.168.100.40 | Rows Distributed to Wrapping Leg 1
18 | [TTM147]FXX1_SVProd3D_Hmi.Counter.dn_ProdTooShort |  | Var | ComData_TTM_147_Alpha_To_Skynet.Status_Bits[21] | 10.168.100.40 | Rows Distributed to Wrapping Leg 2
19 | [TTM147]DA_Ctr_Iface.dn_FillingLevelPercent |  | Var | ComData_TTM_147_Alpha_To_Skynet.Status_Bits[22] | 10.168.100.40 | Buffer Fill Level
20 | [TTM147]HMI_Cmd.Dn_StartHoursShift1 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[0] | 10.168.100.40 | Start Time Hours Shift 1
21 | [TTM147]HMI_Cmd.Dn_StartMinutesShift1 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[1] | 10.168.100.40 | Start Time Minutes Shift 1
22 | [TTM147]HMI_Cmd.Dn_StartHoursShift2 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[2] | 10.168.100.40 | Start Time Hours Shift 2
23 | [TTM147]HMI_Cmd.Dn_StartMinutesShift2 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[3] | 10.168.100.40 | Start Time Minutes Shift 2
24 | [TTM147]HMI_Cmd.Dn_StartHoursShift3 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[4] | 10.168.100.40 | Start Time Hours Shift 3
25 | [TTM147]HMI_Cmd.Dn_StartMinutesShift3 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[5] | 10.168.100.40 | Start Time Minutes Shift 3
26 | [TTM147]HMI_Cmd.Dn_EndHoursShift1 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[6] | 10.168.100.40 | End Time Hours Shift 1
27 | [TTM147]HMI_Cmd.Dn_EndMinutesShift1 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[7] | 10.168.100.40 | End Time Minutes Shift 1
28 | [TTM147]HMI_Cmd.Dn_EndHoursShift2 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[8] | 10.168.100.40 | End Time Hours Shift 2
29 | [TTM147]HMI_Cmd.Dn_EndMinutesShift2 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[9] | 10.168.100.40 | End Time Minutes Shift 2
30 | [TTM147]HMI_Cmd.Dn_EndHoursShift3 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[10] | 10.168.100.40 | End Time Hours Shift 3
31 | [TTM147]HMI_Cmd.Dn_EndMinutesShift3 |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[11] | 10.168.100.40 | End Time Minutes Shift 3
32 | [TTM147]HMI_dn_Hour |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[12] | 10.168.100.40 | Current Hour In Processor
33 | [TTM147]HMI_dn_Minute |  | Var | ComData_TTM_147_Alpha_To_Skynet.Parameters[13] | 10.168.100.40 | Current Minute In Processor
34 | [TTM147]SM.Errors.DynText.List[0].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[0] | 10.168.100.40 | Dynamic Text Fault List 0
35 | [TTM147]SM.Errors.DynText.List[1].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[1] | 10.168.100.40 | Dynamic Text Fault List 1
36 | [TTM147]SM.Errors.DynText.List[2].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[2] | 10.168.100.40 | Dynamic Text Fault List 2
37 | [TTM147]SM.Errors.DynText.List[3].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[3] | 10.168.100.40 | Dynamic Text Fault List 3
38 | [TTM147]SM.Errors.DynText.List[4].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[4] | 10.168.100.40 | Dynamic Text Fault List 4
39 | [TTM147]SM.Errors.DynText.List[5].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[5] | 10.168.100.40 | Dynamic Text Fault List 5
40 | [TTM147]SM.Errors.DynText.List[6].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[6] | 10.168.100.40 | Dynamic Text Fault List 6
41 | [TTM147]SM.Errors.DynText.List[7].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[7] | 10.168.100.40 | Dynamic Text Fault List 7
42 | [TTM147]SM.Errors.DynText.List[8].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[8] | 10.168.100.40 | Dynamic Text Fault List 8
43 | [TTM147]SM.Errors.DynText.List[9].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[9] | 10.168.100.40 | Dynamic Text Fault List 9
44 | [TTM147]SM.Errors.FixText.List[0].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[30] | 10.168.100.40 | Fixed Text Fault List 0
45 | [TTM147]SM.Errors.FixText.List[1].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[31] | 10.168.100.40 | Fixed Text Fault List 1
46 | [TTM147]SM.Errors.FixText.List[2].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[32] | 10.168.100.40 | Fixed Text Fault List 2
47 | [TTM147]SM.Errors.FixText.List[3].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[33] | 10.168.100.40 | Fixed Text Fault List 3
48 | [TTM147]SM.Errors.FixText.List[4].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[34] | 10.168.100.40 | Fixed Text Fault List 4
49 | [TTM147]SM.Errors.FixText.List[5].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[35] | 10.168.100.40 | Fixed Text Fault List 5
50 | [TTM147]SM.Errors.FixText.List[6].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[36] | 10.168.100.40 | Fixed Text Fault List 6
51 | [TTM147]SM.Errors.FixText.List[7].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[37] | 10.168.100.40 | Fixed Text Fault List 7
52 | [TTM147]SM.Errors.FixText.List[8].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[38] | 10.168.100.40 | Fixed Text Fault List 8
53 | [TTM147]SM.Errors.FixText.List[9].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[39] | 10.168.100.40 | Fixed Text Fault List 9
54 | [TTM147]SM.Errors.FixText.List[10].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[40] | 10.168.100.40 | Fixed Text Fault List 10
55 | [TTM147]SM.Errors.FixText.List[11].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[41] | 10.168.100.40 | Fixed Text Fault List 11
56 | [TTM147]SM.Errors.FixText.List[12].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[42] | 10.168.100.40 | Fixed Text Fault List 12
57 | [TTM147]SM.Errors.FixText.List[13].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[43] | 10.168.100.40 | Fixed Text Fault List 13
58 | [TTM147]SM.Errors.FixText.List[14].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[44] | 10.168.100.40 | Fixed Text Fault List 14
59 | [TTM147]SM.Errors.FixText.List[15].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[45] | 10.168.100.40 | Fixed Text Fault List 15
60 | [TTM147]SM.Errors.FixText.List[16].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[46] | 10.168.100.40 | Fixed Text Fault List 16
61 | [TTM147]SM.Errors.FixText.List[17].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[47] | 10.168.100.40 | Fixed Text Fault List 17
62 | [TTM147]SM.Errors.FixText.List[18].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[48] | 10.168.100.40 | Fixed Text Fault List 18
63 | [TTM147]SM.Errors.FixText.List[19].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[49] | 10.168.100.40 | Fixed Text Fault List 19
64 | [TTM147]SM.Errors.FixText.List[20].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[50] | 10.168.100.40 | Fixed Text Fault List 20
65 | [TTM147]SM.Errors.FixText.List[21].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[51] | 10.168.100.40 | Fixed Text Fault List 21
66 | [TTM147]SM.Errors.FixText.List[22].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[52] | 10.168.100.40 | Fixed Text Fault List 22
67 | [TTM147]SM.Errors.FixText.List[23].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[53] | 10.168.100.40 | Fixed Text Fault List 23
68 | [TTM147]SM.Errors.FixText.List[24].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[54] | 10.168.100.40 | Fixed Text Fault List 24
69 | [TTM147]SM.Errors.FixText.List[25].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[55] | 10.168.100.40 | Fixed Text Fault List 25
70 | [TTM147]SM.Errors.FixText.List[26].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[56] | 10.168.100.40 | Fixed Text Fault List 26
71 | [TTM147]SM.Errors.FixText.List[27].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[57] | 10.168.100.40 | Fixed Text Fault List 27
72 | [TTM147]SM.Errors.FixText.List[28].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[58] | 10.168.100.40 | Fixed Text Fault List 28
73 | [TTM147]SM.Errors.FixText.List[29].dn_ID |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[59] | 10.168.100.40 | Fixed Text Fault List 29
74 | [TTM147]SM.Errors.DynText.dn_LastPos |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[60] | 10.168.100.40 | Position of Last stored position in Dyn List
75 | [TTM147]SM.Errors.FixText.dn_LastPos |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[61] | 10.168.100.40 | Position of Last stored position in Fix List
76 | [TTM147]SM.Errors.DynText.dn_EmptyPos |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[62] | 10.168.100.40 | Position of Next stored position in Dyn List
77 | [TTM147]SM.Errors.FixText.dn_EmptyPos |  | Var | ComData_TTM_147_Alpha_To_Skynet.Fault_data[63] | 10.168.100.40 | Position of Next stored position in Fix List
PLC 2 Data
1 | [TTM147]UIFace_DXX_OUT.b_ready |  | 1 | ComData_TTM_147_2_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.40 | FXX Infeed Runnning
2 | [TTM147]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdOut |  | Var | ComData_TTM_147_2_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.40 | Product count into wrapper
3
4
5
6
7
8
9
10
PLC 3 Data
1 | [TTM147]UIFace_DXX_OUT.b_ready |  | 1 | ComData_TTM_147_2_Alpha_To_Skynet.Status_Bits[0].0 | 10.168.100.40 | FXX Infeed Runnning
2 | [TTM147]STA_Hmi.PresentShift.Performance_3dRej.dn_ProdOut |  | Var | ComData_TTM_147_2_Alpha_To_Skynet.Status_Bits[10] | 10.168.100.40 | Product count into wrapper

## Chocotech Kitchen
Caraflex Data
1 | [CT_PLC]TIC050_17_PID[1].SP.New_Setpoint | Var | ComData_Chocotech_To_Skynet.Parameters[0] | 10.168.100.1 | Steam Pressure Setpoint (psi)
2 | [CT_PLC]TIC050_17_PID[0].SP.Actual_Setpoint | Var | ComData_Chocotech_To_Skynet.Parameters[1] | 10.168.100.1 | Temperature Setpoint (°F)
3 | [CT_PLC]NC040_12.Reference | Var | ComData_Chocotech_To_Skynet.Parameters[2] | 10.168.100.1 | Sucrofilm Speed (Hz)
4 | [CT_PLC]LIC050_18_PID.SP.Req_Setpoint | Var | ComData_Chocotech_To_Skynet.Parameters[3] | 10.168.100.1 | Caraflex Level Setpoint (%)
5 | [CT_PLC]NC085_12.Reference | Var | ComData_Chocotech_To_Skynet.Parameters[4] | 10.168.100.1 | Melt Tank Stirrer Speed Setpoint (Hz)
6 | [CT_PLC]Miscellanous_Real[2] | Var | ComData_Chocotech_To_Skynet.Parameters[5] | 10.168.100.1 | Melt Tank Temperature Setpoint (°F)
7 | [CT_PLC]TIC068_17_PID_AOI[0].SP | Var | ComData_Chocotech_To_Skynet.Parameters[6] | 10.168.100.1 | Sucrotherm Cooling Water Setpoint (°F)
8 | [CT_PLC]FIC030_15_PID.SP.Req_Setpoint | Var | ComData_Chocotech_To_Skynet.Parameters[7] | 10.168.100.1 | Supply Rate to Sucrotherm (kg/hr)
9 | [CT_PLC]FIC090_15_PID.SP.New_Setpoint | Var | ComData_Chocotech_To_Skynet.Parameters[8] | 10.168.100.1 | Supply Rate to Alpha (kg/hr)
10 | [CT_PLC]FIC100_15_PID.SP.New_Setpoint | Var | ComData_Chocotech_To_Skynet.Parameters[9] | 10.168.100.1 | Supply Rate to Bravo (kg/hr)
11 | [CT_PLC]FIC110_15_PID.SP.New_Setpoint | Var | ComData_Chocotech_To_Skynet.Parameters[10] | 10.168.100.1 | Supply Rate to Charlie (kg/hr)
12 | [CT_PLC]TIC145_24_EM.Temperature_Water | Var | ComData_Chocotech_To_Skynet.Parameters[11] | 10.168.100.1 | Temperature Unit 1 Setpoint (°F)
13 | [CT_PLC]TIC146_24_EM.Temperature_Water | Var | ComData_Chocotech_To_Skynet.Parameters[12] | 10.168.100.1 | Temperature Unit 2 Setpoint (°F)
14 | [CT_PLC]TIC147_24_EM.Temperature_Water | Var | ComData_Chocotech_To_Skynet.Parameters[13] | 10.168.100.1 | Temperature Unit 3 Setpoint (°F)
15 | [CT_PLC]TIC148_24_EM.Temperature_Water | Var | ComData_Chocotech_To_Skynet.Parameters[14] | 10.168.100.1 | Temperature Unit 4 Setpoint (°F)
| [CT_PLC]TIC050_17_PID_AOI[1].PV | Var | ComData_Chocotech_To_Skynet.Process_Values[0] | 10.168.100.1 | Actual Steam Pressure (psi)
| [CT_PLC]TIC050_17_AOI.Scaled | Var | ComData_Chocotech_To_Skynet.Process_Values[1] | 10.168.100.1 | Actual Temperature (°F)
| [CT_PLC]TIC050_17_ATMOS.SP_Temperature_Corrected | Var | ComData_Chocotech_To_Skynet.Process_Values[2] | 10.168.100.1 | Calculated Temperature Correction (°F)
| [CT_PLC]NC040_12.Feedback | Var | ComData_Chocotech_To_Skynet.Process_Values[3] | 10.168.100.1 | Sucrofilm Actual Speed (Hz)
| [CT_PLC]LIC050_18_PID_AOI.PV | Var | ComData_Chocotech_To_Skynet.Process_Values[4] | 10.168.100.1 | Caraflex Actual Level (%)
| [CT_PLC]PIC050_19_AOI_Scaled | Var | ComData_Chocotech_To_Skynet.Process_Values[5] | 10.168.100.1 | Vapor Pressure (mbar)
| [CT_PLC]NC085_12.Feedback | Var | ComData_Chocotech_To_Skynet.Process_Values[6] | 10.168.100.1 | Melt Tank Stirrer Speed Actual (Hz)
| [CT_PLC]LI085_15_AOI.Scaled | Var | ComData_Chocotech_To_Skynet.Process_Values[7] | 10.168.100.1 | Melt Tank Level (%)
| [CT_PLC]TI085_17_AOI.Scaled | Var | ComData_Chocotech_To_Skynet.Process_Values[8] | 10.168.100.1 | Melt Tank Actual Temperature (°F)
| [CT_PLC]LI080_15_AOI.Scaled | Var | ComData_Chocotech_To_Skynet.Process_Values[9] | 10.168.100.1 | Day Tank Level (%)
| [CT_PLC]LI075_15_AOI.Scaled | Var | ComData_Chocotech_To_Skynet.Process_Values[10] | 10.168.100.1 | Reclaim Tank Level (%)
| [CT_PLC]TIC068_17_PID_AOI[0].PV | Var | ComData_Chocotech_To_Skynet.Process_Values[11] | 10.168.100.1 | Sucrotherm Cooling Water Actual Temperature (°F)
| [CT_PLC]TI064_17_AOI.SCALED | Var | ComData_Chocotech_To_Skynet.Process_Values[12] | 10.168.100.1 | Sucrotherm Transfer Temperature 1 (°F)
| [CT_PLC]TI060_17_AOI.SCALED | Var | ComData_Chocotech_To_Skynet.Process_Values[13] | 10.168.100.1 | Sucrotherm Transfer Temperature 2 (°F)
| [CT_PLC]FIC030_15_PID_AOI.PV | Var | ComData_Chocotech_To_Skynet.Process_Values[14] | 10.168.100.1 | Supply Rate to Sucrofilm Actual (kg/hr)
| [CT_PLC]FIC090_15_PID_AOI.PV | Var | ComData_Chocotech_To_Skynet.Process_Values[15] | 10.168.100.1 | Supply Rate to Alpha Actual (kg/hr)
| [CT_PLC]FIC100_15_PID_AOI.PV | Var | ComData_Chocotech_To_Skynet.Process_Values[16] | 10.168.100.1 | Supply Rate to Bravo Actual (kg/hr)
| [CT_PLC]FIC110_15_PID_AOI.PV | Var | ComData_Chocotech_To_Skynet.Process_Values[17] | 10.168.100.1 | Supply Rate to Charlie Actual (kg/hr)
| [CT_PLC]TIC145_24_AOI.Scaled_Factor | Var | ComData_Chocotech_To_Skynet.Process_Values[18] | 10.168.100.1 | Tempering Unit 1 Actual Temperature (°F)
| [CT_PLC]TIC146_24_AOI.Scaled_Factor | Var | ComData_Chocotech_To_Skynet.Process_Values[19] | 10.168.100.1 | Tempering Unit 2 Actual Temperature (°F)
| [CT_PLC]TIC147_24_AOI.Scaled_Factor | Var | ComData_Chocotech_To_Skynet.Process_Values[20] | 10.168.100.1 | Tempering Unit 3 Actual Temperature (°F)
| [CT_PLC]TIC148_24_AOI.Scaled_Factor | Var | ComData_Chocotech_To_Skynet.Process_Values[21] | 10.168.100.1 | Tempering Unit 4 Actual Temperature (°F)
| [CT_PLC]TI140_57_AOI.SCALED | Var | ComData_Chocotech_To_Skynet.Process_Values[22] | 10.168.100.1 | CIP Tank 1 Temperature Actual
| [CT_PLC]TI1401_71_AOI.SCALED | Var | ComData_Chocotech_To_Skynet.Process_Values[23] | 10.168.100.1 | CIP Tank 2 Temperature Actual
| [CT_PLC]TI1402_71_AOI.SCALED | Var | ComData_Chocotech_To_Skynet.Process_Values[24] | 10.168.100.1 | CIP Tank 3 Temperature Actual
| [CT_PLC]NC091_20_Slave.Enabled | 1 | ComData_Chocotech_To_Skynet.Status_Bits[0].10 | 10.168.100.1 | NC091/20 Alpha
| [CT_PLC]NC101_40_Slave.Enabled | 1 | ComData_Chocotech_To_Skynet.Status_Bits[0].11 | 10.168.100.1 | NC101/40 Bravo
| [CT_PLC]NC111_40_Slave.Enabled | 1 | ComData_Chocotech_To_Skynet.Status_Bits[0].12 | 10.168.100.1 | NC111/40 Charlie